## Energy Calcs
Energy Consumption | [29 empty] | Flow, gpm | [20 empty] | Pressure, psig | [7 empty] | Flux, GFD
[5 empty] | Cases | [24 empty] | 1st Pass | [11 empty] | 2nd Pass | [8 empty] | 1st Pass |  |  |  | 2nd Pass | [5 empty] | 1st Pass High Pressure Pump Curve
[5 empty] | DESIGN - TRAIN | years | TDS | temp | # Trains |  | Per Train PV | 0 | 0 | pH |  | TDS | 0 | Chloride | 0 | Bromide | 0 | Boron | 0 | Sodium | 0 | Recovery (%) | Recovery |  | # Trains in | TOTAL inlet to RO | inlet | inlet | per hp pump | ERD Recic | per ERD | brine to pumps | per ERD pump | brine to ERD | total | front permeate | CIP | inlet | inlet | 1st permeate | 1st brine | 2st permeate | 2ns pass Brine | 2st brine per train | permeate | permeate | inlet | brine | front | rear | inlet | 1st permeate | Brine | 2nd permeate | 1st | 2nd
| Default VFD efficiency | 0.97 |  |  | ref |  | mg/l | degC | 1st | 2nd | 1st pass | 1st stg | 2nd stg | 1st | 2nd | mg/l |  | Proj mg/L | War mg/L | Proj mg/L | War mg/L | Proj mg/L | War mg/L | Proj mg/L | War mg/L | total | 1st | 2nd | Operation | - BRINE 2nd pass | membranes | to HPP | 0 | pump | (pump) | 0 | 0 |  | permeate |  |  |  | per 2ND pass |  |  |  | 0
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 33.6k | 12 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 71 |  | 40.2 | 410.04 | 0 | 0 | 0.37 | 183.7938 | 26.8 | 0 |  | 45 | 90 | 7 + 2 | 15000 | 15153 | 6839.1 |  | 8314 |  |  |  |  | 6666.7 |  |  | 1528 | [6 empty] | 1375 |  | 721 | 713 |  |  | 76.6 |  | 56.1 |  | 7.1 | 8.2
Cartridge Filter Feed Pumps | Total gpm | 15000
| psi | 18 |  |  | 9.6 SWC5LD ESPA2MAX | 5 | Max | 20 | 6 | 2 | 426 | 54 | 24 | 8.3 | 10.2 | 86.3 |  | 48.4 | 493.68 | 0 | 0 | 0.43 | 215.3526 | 32.2 | 0 |  | 45 | 90 | 6 + 2 | 15043 | 15230 | 6873.9 |  | 8356.8 |  |  |  |  | 6666.7 |  |  | 1875 | [6 empty] | 1687.5 |  | 849.8 | 839.9 |  |  | 88.6 |  | 63 |  | 8.3 | 10.1
| # Pumps | 4 |  |  | 9.6 SWC5LD ESPA2MAX | 5 | Max | 8 | 6 | 2 | 426 | 54 | 24 | 8.3 | 10.2 | 85.8 |  | 48 | 489.6 | 0 | 0 | 0.35 | 175.287 | 32.1 | 0 |  | 45 | 90 | 6 + 2 | 14890 | 14952 | 6748.5 |  | 8204.4 |  |  |  |  | 6666.7 |  |  | 625 | [6 empty] | 563 |  | 968.7 | 958.7 |  |  | 42 |  | 34.1 |  | 8.1 | 3.4
| Pump Flow, gpm | 3750
| pump eff | 0.78 |  |  | 9.6 SWC5LD ESPA2MAX | 3.5 | Max | 20 | 6 | 2 | 426 | 54 | 24 | 8.3 | 10.2 | 87 |  | 48.7 | 496.74 | 0 | 0 | 0.44 | 220.3608 | 32.4 | 0 |  | 45 | 90 | 6 + 2 | 15034 | 15215 | 6867 |  | 8348 |  |  |  |  | 6666.7 |  |  | 1805.6 | [6 empty] | 1625 |  | 833.8 | 823.9 |  |  | 83.4 |  | 59.6 |  | 8.3 | 9.7
| motor eff | 0.948 |  |  | 9.6 SWC5LD ESPA2MAX | 3.5 | Max | 8 | 6 | 2 | 426 | 54 | 24 | 8.3 | 10.2 | 87.6 |  | 49.1 | 500.82 | 0 | 0 | 0.35 | 175.287 | 32.8 | 0 |  | 45 | 90 | 6 + 2 | 14881 | 14937 | 6741.6 |  | 8195.9 |  |  |  |  | 6666.7 |  |  | 555.6 | [6 empty] | 500 |  | 940.2 | 930.3 |  |  | 37.5 |  | 30.6 |  | 8.1 | 3
| Pump kW | 163.3724
| kW/1000 gal product | 0.40843 |  |  | 9.6 SWC5LD ESPA2MAX | 5 | Avg | 20 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 79.6 |  | 44.9 | 457.98 | 0 | 0 | 0.46 | 230.3772 | 30 | 0 |  | 45 | 90 | 6 + 2 | 15043 | 15230 | 6873.9 |  | 8356.8 |  |  |  |  | 6666.7 |  |  | 1875 | [6 empty] | 1687.5 |  | 774.4 | 764.4 |  |  | 87 |  | 61.1 |  | 8.3 | 10.1
[5 empty] | 9.6 SWC5LD ESPA2MAX | 5 | Avg | 18 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 84 |  | 47.4 | 483.48 | 0 | 0 | 0.46 | 230.3772 | 31.6 | 0 |  | 45 | 90 | 6 + 2 | 15000 | 15135 | 6839.1 |  | 8314.4 |  |  |  |  | 6666.7 |  |  | 1527.8 | [6 empty] | 1375 |  | 785.3 | 775.3 |  |  | 75.1 |  | 55 |  | 8.2 | 8.2
RO Feed Pumps | Total gpm | 6839.1 |  |  | 9.6 SWC5LD ESPA2MAX | 5 | Avg | 15 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 89 |  | 50.2 | 512.04 | 0 | 0 | 0.46 | 230.3772 | 33.5 | 0 |  | 45 | 90 | 6 + 2 | 14941 | 15045 | 6790.3 |  | 8255.2 |  |  |  |  | 6666.7 |  |  | 1041.7 | [6 empty] | 937.5 |  | 806.5 | 796.6 |  |  | 57 |  | 44.1 |  | 8.2 | 5.6
| psi | 714 |  |  | 9.6 SWC5LD ESPA2MAX | 5 | Avg | 13 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 91.7 |  | 51.7 | 527.34 | 0 | 0 | 0.46 | 230.3772 | 34.5 | 0 |  | 45 | 90 | 6 + 2 | 14907 | 14983 | 6762.5 |  | 8221.3 |  |  |  |  | 6666.7 |  |  | 763.9 | [6 empty] | 687.5 |  | 824.8 | 814.8 |  |  | 45.3 |  | 36.1 |  | 8.1 | 4.1
| # Pumps | 7 |  |  | 9.6 SWC5LD ESPA2MAX | 5 | Avg | 12 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 62 |  | 34.9 | 355.98 | 0 | 0 | 0.32 | 160.2624 | 23.3 | 0 |  | 45 | 90 | 6 + 2 | 15030 | 15207 | 6863.5 |  | 8344.1 |  |  |  |  | 6666.7 |  |  | 1770.8 | [6 empty] | 1593.8 |  | 835.7 | 825.5 |  |  | 96.6 |  | 70.9 |  | 8.3 | 9.6
| Pump Flow, gpm | 977.0143 |  |  | 9.6 SWC5LD ESPA2MAX | 5 | Avg | 10 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 61.7 |  | 34.8 | 354.96 | 0 | 0 | 0.31 | 155.2542 | 23.2 | 0 |  | 45 | 90 | 6 + 2 | 15005 | 15161 | 6842.6 |  | 8318.7 |  |  |  |  | 6666.7 |  |  | 1562.5 | [6 empty] | 1406.3 |  | 860.7 | 850.5 |  |  | 89.8 |  | 67.5 |  | 8.2 | 8.4
| pump eff | 0.81 |  |  | 9.6 SWC5LD ESPA2MAX | 5 | Avg | 8 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 61.5 |  | 34.7 | 353.94 | 0 | 0 | 0.3 | 150.246 | 23.2 | 0 |  | 45 | 90 | 6 + 2 | 14975 | 15107 | 6818.2 |  | 8289 |  |  |  |  | 6666.7 |  |  | 1319.4 | [6 empty] | 1187.5 |  | 891 | 880.7 |  |  | 80.2 |  | 61.9 |  | 8.2 | 7.1
| motor eff | 0.965
| Pump kW | 2795.1353 |  |  | 9.6 SWC5LD ESPA2MAX | 3.5 | Avg | 20 | 6 | 2 | 426 | 54 | 24 | 8 | 10.4 | 51.4 |  | 29 | 295.8 | 0 | 0 | 0.33 | 165.2706 | 19.3 | 0 |  | 45 | 90 | 6 + 2 | 15187 | 15493 | 6992.3 |  | 8500.7 |  |  |  |  | 6666.7 |  |  | 3055.6 | [6 empty] | 2750 |  | 757.6 | 747.4 |  |  | 132.9 |  | 83.1 |  | 8.4 | 16.5
| kW/1000 gal product | 6.9878 |  |  | 9.6 SWC5LD ESPA2MAX | 3.5 | Avg | 20 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 80.2 |  | 45.2 | 461.04 | 0 | 0 | 0.46 | 230.3772 | 30.1 | 0 |  | 45 | 90 | 6 + 2 | 15034 | 15215 | 6866.9 |  | 8348.3 |  |  |  |  | 6666.7 |  |  | 1805.6 | [6 empty] | 1625 |  | 759.3 | 749.5 |  |  | 81.8 |  | 57.5 |  | 8.3 | 9.7
[5 empty] | 9.6 SWC5LD ESPA2MAX | 3.5 | Avg | 18 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 56.7 |  | 32 | 326.4 | 0 | 0 | 0.33 | 165.2706 | 21.3 | 0 |  | 45 | 90 | 6 + 2 | 15128 | 15385 | 6943.6 |  | 8441.4 |  |  |  |  | 6666.7 |  |  | 2569.4 | [6 empty] | 2312.5 |  | 768.1 | 758 |  |  | 117.1 |  | 77.1 |  | 8.4 | 13.9
ERD Recirc Pumps | Total gpm | 8314 |  |  | 9.6 SWC5LD ESPA2MAX | 3.5 | Avg | 18 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 82.6 |  | 46.6 | 475.32 | 0 | 0 | 0.46 | 230.3772 | 31.1 | 0 |  | 45 | 90 | 6 + 2 | 15000 | 15153 | 6839.1 |  | 8314.1 |  |  |  |  | 6666.7 |  |  | 1527.8 | [6 empty] | 1375 |  | 769 | 759.1 |  |  | 73 |  | 53.1 |  | 8.2 | 8.2
| psi | 31.025 |  |  | 9.6 SWC5LD ESPA2MAX | 3.5 | Avg | 16 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 59 |  | 33.3 | 339.66 | 0 | 0 | 0.33 | 165.2706 | 22.2 | 0 |  | 45 | 90 | 6 + 2 | 15094 | 15323 | 6915.7 |  | 8408 |  |  |  |  | 6666.7 |  |  | 2291.7 | [6 empty] | 2062.5 |  | 780.3 | 770.2 |  |  | 109.4 |  | 74.5 |  | 8.3 | 12.4
| # pumps | 7 |  |  | 9.6 SWC5LD ESPA2MAX | 3.5 | Avg | 15 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 88.3 |  | 49.8 | 507.96 | 0 | 0 | 0.46 | 230.3772 | 33.3 | 0 |  | 45 | 90 | 6 + 2 | 14941 | 15045 | 6790.3 |  | 8255.2 |  |  |  |  | 6666.7 |  |  | 1041.7 | [6 empty] | 937.5 |  | 788 | 778.1 |  |  | 55.5 |  | 42.8 |  | 8.2 | 5.6
| Pump Flow, gpm | 1187.7143 |  |  | 9.6 SWC5LD ESPA2MAX | 3.5 | Avg | 14 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 60.5 |  | 34.1 | 347.82 | 0 | 0 | 0.33 | 165.2706 | 22.8 | 0 |  | 45 | 90 | 6 + 2 | 15060 | 15261 | 6888 |  | 8374 |  |  |  |  | 6666.7 |  |  | 2013.9 | [6 empty] | 1812.5 |  | 795.4 | 785.3 |  |  | 100.9 |  | 71.1 |  | 8.3 | 10.9
| pump eff | 0.8 |  |  | 9.6 SWC5LD ESPA2MAX | 3.5 | Avg | 13 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 91.2 |  | 51.5 | 525.3 | 0 | 0 | 0.46 | 230.3772 | 34.4 | 0 |  | 45 | 90 | 6 + 2 | 14907 | 14983 | 6762.5 |  | 8221.3 |  |  |  |  | 6666.7 |  |  | 763.9 | [6 empty] | 687.5 |  | 804.4 | 794.5 |  |  | 44.3 |  | 35.2 |  | 8.1 | 4.1
| motor eff | 0.942 |  |  | 9.6 SWC5LD ESPA2MAX | 3.5 | Avg | 12 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 61.9 |  | 34.9 | 355.98 | 0 | 0 | 0.32 | 160.2624 | 23.3 | 0 |  | 45 | 90 | 6 + 2 | 15026 | 15199 | 6860 |  | 8340 |  |  |  |  | 6666.7 |  |  | 1736.1 | [6 empty] | 1562.5 |  | 814 | 803.8 |  |  | 91.6 |  | 66.6 |  | 8.2 | 9.4
| Pump kW | 153.1436 |  |  | 9.6 SWC5LD ESPA2MAX | 3.5 | Avg | 10 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 61.8 |  | 34.9 | 355.98 | 0 | 0 | 0.31 | 155.2542 | 23.3 | 0 |  | 45 | 90 | 6 + 2 | 15000 | 15153 | 6839.1 |  | 8314.4 |  |  |  |  | 6666.7 |  |  | 1527.8 | [6 empty] | 1375 |  | 836.6 | 826.5 |  |  | 84.8 |  | 63.3 |  | 8.2 | 8.2
| kW/1000 gal product | 0.38286 |  |  | 9.6 SWC5LD ESPA2MAX | 3.5 | Avg | 8 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 62.4 |  | 35.2 | 359.04 | 0 | 0 | 0.3 | 150.246 | 23.4 | 0 |  | 45 | 90 | 6 + 2 | 14966 | 15091 | 6811.2 |  | 8280.6 |  |  |  |  | 6666.7 |  |  | 1250 | [6 empty] | 1125 |  | 864.1 | 854 |  |  | 73.5 |  | 56.5 |  | 8.2 | 6.7
2nd Pass RO Feed Pumps | Total gpm | 1528 |  |  | 9.6 SWC5LD ESPA2MAX | 5 | 33.6 | 12 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 62.1 |  | 35 | 357 | 0 | 0 | 0.32 | 160.2624 | 23.4 | 0 |  | 45 | 90 | 6 + 2 | 15022 | 15192 | 6856.5 |  | 8335.6 |  |  |  |  | 6666.7 |  |  | 1701.4 | [6 empty] | 1531.3 |  | 819.7 | 809.5 |  |  | 92.8 |  | 68.3 |  | 8.3 | 9.2
| psi | 82.6 |  | 189.98 | 9.6 SWC5LD ESPA2MAX | 3.5 | 33.6 | 12 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 62.1 |  | 35 | 357 | 0 | 0 | 0.32 | 160.2624 | 23.4 | 0 |  | 45 | 90 | 6 + 2 | 15017 | 15184 | 6853 |  | 8331 |  |  |  |  | 6666.7 |  |  | 1667 | [6 empty] | 1500 |  | 797.6 | 787.5 |  |  | 87.8 |  | 64.1 |  | 8.2 | 9
| # pumps | 2
| Pump Flow, gpm | 764 |  |  | 9.6 SWC5LD ESPA2MAX | 0 | Max | 18 | 7 | 2 | 497 | 54 | 24 | 8.3 | 10.2 |  |  | 56 | 571.2 | 0 | 0 | 0.49 | 243.4026 | 40.7 | 0 |  | 45 | 90 | 7 + 2 | 14992 | 15138 | 6832.1 |  | 8306 |  |  |  |  | 6666.7 |  |  | 1458.3 | [6 empty] | 1312.5 |  | 780.6 | 773 |  |  | 73.3 |  | 57.6 |  | 7 | 7.9
| pump eff | 0.5 |  |  | 9.6 SWC5LD ESPA2MAX | 0 | Max | 15 | 7 | 2 | 497 | 54 | 24 | 8.3 | 10.2 | 101.5 |  | 57 | 581.4 | 0 | 0 | 0.47 | 233.4678 | 37.9 | 0 |  | 45 | 90 | 7 + 2 | 14958 | 15076 | 6904 |  | 8272 |  |  |  |  | 6666.7 |  |  | 1180.6 | [6 empty] | 1063 |  | 793.8 | 786.1 |  |  | 65.5 |  | 50.2 |  | 7 | 6.4
| motor eff | 0.963 |  |  | 9.6 SWC5LD ESPA2MAX | 0 | Max | 12 | 7 | 2 | 497 | 54 | 24 | 8.3 | 10.2 | 99.4 |  | 56 | 571.2 | 0 | 0 | 0.43 | 213.5982 | 37.2 | 0 |  | 45 | 90 | 7 + 2 | 14932 | 15030 | 6783.4 |  | 8247 |  |  |  |  | 6666.7 |  |  | 972 | [6 empty] | 875 |  | 809.3 | 801.6 |  |  | 55.9 |  | 44.9 |  | 7 | 5.2
| Pump kW | 117.2803 |  | RO Process(incl CF pump) | 9.6 SWC5LD ESPA2MAX | 0 | Max | 10 | 7 | 2 | 497 | 54 | 24 | 8.3 | 10.2 | 101 |  | 56 | 571.2 | 0 | 0 | 0.42 | 208.6308 | 37.6 | 0 |  | 45 | 90 | 7 + 2 | 14907 | 14983 | 6762.5 |  | 8221 |  |  |  |  | 6666.7 |  |  | 764 | [6 empty] | 688 |  | 823.2 | 815.4 |  |  | 47.8 |  | 39.2 |  | 7 | 4.1
| kW/1000 gal product | 0.2932 | kwh/100 gal | 8.0723 | 9.6 SWC5LD ESPA2MAX | 0 | Max | 8 | 7 | 2 | 497 | 54 | 24 | 8.3 | 10.2 | 101 |  | 57 | 581.4 | 0 | 0 | 0.41 | 203.6634 | 37.9 | 0 |  | 45 | 90 | 7 + 2 | 14881 | 14937 | 6741.6 |  | 8196 |  |  |  |  | 6666.7 |  |  | 556 | [6 empty] | 500 |  | 840.9 | 833 |  |  | 39.1 |  | 32.7 |  | 7 | 3
|  |  | kwh/m3 | 2.1355
Distribution Pumps | Total gpm | 6666.7 |  |  | Note that data in rows that are struck through represent meeting the Maximum Average Permeate Concentrations at temperatures greater than 20C
| psi | 134.6087 |  |  | 9.6 SWC5LD ESPA2MAX | 0 | Avg | 18 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 65 |  | 36.4 | 371.28 | 0 | 0 | 0.38 | 188.7612 | 24.3 | 0 |  | 45 | 90 | 7 + 2 | 15102 | 15338 | 6922.7 |  | 8416 |  |  |  |  | 6666.7 |  |  | 2361 | [6 empty] | 2125 |  | 711 | 703 |  |  | 102 |  | 68 |  | 7.1 | 12.7
| # pumps | 4 |  |  | 9.6 SWC5LD ESPA2MAX | 0 | Avg | 18 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 94.8 |  | 53.6 | 546.72 | 0 | 0 | 0.53 | 263.2722 | 35.6 | 0 |  | 56 | 90 | 7 + 2 | 14983 | 15122 | 6825.2 |  | 8297.5 |  |  |  |  | 6666.7 |  |  | 1388.9 | [6 empty] | 1250 |  | 712.9 | 705.2 |  |  | 67.5 |  | 51.4 |  | 7 | 7.5
| Pump Flow, gpm | 1666.675 |  |  | 9.6 SWC5LD ESPA2MAX | 0 | Avg | 15 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 69 |  | 39 | 397.8 | 0 | 0 | 0.38 | 188.7612 | 26 | 0 |  | 45 | 90 | 7 + 2 | 15051 | 15246 | 6880.9 |  | 8365.2 |  |  |  |  | 6666.7 |  |  | 1944 | [6 empty] | 1750 |  | 721.8 | 713.9 |  |  | 90.4 |  | 63.1 |  | 7.1 | 10.5
| pump eff | 0.78 |  |  | 9.6 SWC5LD ESPA2MAX | 0 | Avg | 15 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 102.4 |  | 57.8 | 589.56 | 0 | 0 | 0.53 | 263.2722 | 38.5 | 0 |  | 45 | 90 | 7 + 2 | 14932 | 15030 | 6783.4 |  | 8246.7 |  |  |  |  | 6666.7 |  |  | 972.2 | [6 empty] | 875 |  | 723.3 | 715.6 |  |  | 54 |  | 43.5 |  | 7 | 5.2
| motor eff | 0.961 |  |  | 9.6 SWC5LD ESPA2MAX | 0 | Avg | 13 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 103.6 |  | 58.5 | 596.7 | 0 | 0 | 0.52 | 258.3048 | 39 | 0 |  | 45 | 90 | 7 + 2 | 14907 | 14983 | 6762.5 |  | 8221.4 |  |  |  |  | 6666.7 |  |  | 763.9 | [6 empty] | 687.5 |  | 732.8 | 725 |  |  | 46.7 |  | 38.5 |  | 7 | 4.1
| Pump kW | 535.6536 |  |  | 9.6 SWC5LD ESPA2MAX | 0 | Avg | 13 | 7 | 1 | 497 | 27 | 12 | 8 | 10.5 | 109 |  | 61.5 | 627.3 | 0 | 0 | 0.53 | 263.2722 | 41.1 | 0 |  | 45 | 90 | 7 + 1 | 14886 | 14945 | 6745.1 |  | 8200.1 |  |  |  |  | 6666.7 |  |  | 590.3 | [6 empty] | 531.3 |  | 733 | 725.3 |  |  | 64.3 |  | 50.4 |  | 7 | 6.4
| kW/1000 gal product | 1.3391 |  |  | 9.6 SWC5LD ESPA2MAX | 0 | Avg | 12 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 72 |  | 40.5 | 413.1 | 0 | #REF! | 0.37 | 183.7938 | 27 | 0 |  | 45 | 90 | 7 + 2 | 15005 | 15161 | 6843 | #REF! | 8319 | #REF! | #REF! | #REF! | #REF! | 6667.1 | #REF! | #REF! | 1559 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1403 | #REF! | 737.6 | 729.7 | #REF! | #REF! | 78.4 | #REF! | 57 | #REF! | 7.1 | 8.4
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | Avg | 10 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 72 |  | 40.5 | 413.1 | 0 | #REF! | 0.36 | 178.8264 | 27 | 0 |  | 45 | 90 | 7 + 2 | 14983 | 15122 | 6825 |  | 8298 |  |  |  |  | 6666.7 |  |  | 1389 | [6 empty] | 1250 |  | 751.6 | 743.6 |  |  | 73.2 |  | 54.7 |  | 7 | 7.5 | 2nd Pass High Pressure Pump Curve
Total for Pumps | kW/1000 gal product | 9.4114 |  |  | 9.6 SWC5LD ESPA2MAX | 0 | Avg | 8 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 72 |  | 40.5 | 413.1 | 0 | 0 | 0.35 | 173.859 | 27 | 0 |  | 45 | 90 | 7 + 2 | 14958 | 15076 | 6804 |  | 8272 |  |  |  |  | 6666.7 |  |  | 1180.6 | [6 empty] | 1063 |  | 769.2 | 761.2 |  |  | 66 |  | 50 |  | 7 | 6.4
Fixed Energy | kW/1000 gal product | 1.8337 | [16 empty] | 0 |  | #VALUE! |  | 0 |  | 0
Xfrmr losses | kW/1000 gal product | 0.22502
Total | kW/1000 gal product | 11.4702 |  |  | 9.6 SWC5LD ESPA2MAX | 0 | 33.6k | 18 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 65 |  | 36.5 | 372.3 | 0 | 0 | 0.38 | 188.7612 | 24.3 | 0 |  | 45 | 90 | 7 + 2 | 15094 | 15323 | 6916 |  | 8408 |  |  |  |  | 6666.7 |  |  | 2292 | [6 empty] | 2063 |  | 694.4 | 686.6 |  |  | 99.2 |  | 66.1 |  | 7.1 | 12.4
| kwh/m^3 product | 3.0344 |  |  | 9.6 SWC5LD ESPA2MAX | 0 | 33.6k | 18 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 95.2 |  | 53.8 | 548.76 | 0 | 0 | 0.53 | 263.2722 | 35.8 | 0 |  | 45 | 90 | 7 + 2 | 14975 | 15107 | 6818.2 |  | 8289 |  |  |  |  | 6666.7 |  |  | 1319.4 | [6 empty] | 1187.5 |  | 696.2 | 688.5 |  |  | 64.8 |  | 49.7 |  | 7 | 7.1
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 33.6k | 18 | 7 | 1 | 497 | 27 | 12 | 8 | 10.5 | 99.3 |  | 56 | 571.2 | 0 | 0 | 0.53 | 263.2722 | 37.4 | 0 |  | 45 | 90 | 7 + 1 | 14964 | 15068 | 6800.8 |  | 8267.9 |  |  |  |  | 6666.7 |  |  | 1145.8 | [6 empty] | 1031.3 |  | 696.5 | 688.8 |  |  | 103.7 |  | 71.8 |  | 7 | 12.4
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 33.6k | 15 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 70 |  | 39.2 | 399.84 | 0 | 0 | 0.38 | 188.7612 | 26.1 | 0 |  | 45 | 90 | 7 + 2 | 15043 | 15230 | 6874 |  | 8357 |  |  |  |  | 6666.7 |  |  | 1875 | [6 empty] | 1688 |  | 705.2 | 697.3 |  |  | 87.2 |  | 61.1 |  | 7.1 | 10.1
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 33.6k | 15 | 7 | 1 | 497 | 27 | 12 | 8 | 10.5 | 105.4 |  | 59.5 | 606.9 | 0 | 0 | 0.53 |  | 39.7 | 0 |  | 45 | 90 | 7 + 1 | 14907 | 14983 | 6762.5 |  | 8221.3 |  |  |  |  | 6666.7 |  |  | 763.9 | [6 empty] | 687.5 |  | 706.8 | 699.1 |  |  | 77 |  | 58.1 |  | 7 | 8.2
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 33.6k | 13 | 7 | 1 | 497 | 27 | 12 | 8 | 10.5 | 108.2 |  | 61 | 622.2 | 0 | 0 | 0.53 | 263.2722 | 40.7 | 0 |  | 45 | 90 | 7 + 1 | 14881 | 14937 | 6741.6 |  | 8195.9 |  |  |  |  | 6666.7 |  |  | 555.6 | [6 empty] | 500 |  | 716.4 | 708.6 |  |  | 60.9 |  | 48 |  | 7 | 6
| ERD Recirc Pump Curve |  |  |  | 9.6 SWC5LD ESPA2MAX | 0 | 33.6k | 12 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 71 |  | 40.2 | 410.04 | 0 | 0 | 0.37 | 183.7938 | 26.8 | 0 |  | 45 | 90 | 7 + 2 | 15000 | 15153 | 6839.1 |  | 8314 |  |  |  |  | 6666.7 |  |  | 1528 | [6 empty] | 1375 |  | 721 | 713 |  |  | 76.6 |  | 56.1 |  | 7.1 | 8.2
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 33.6k | 10 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 72 |  | 40.7 | 415.14 | 0 | 0 | 0.36 | 178.8264 | 27.1 | 0 |  | 45 | 90 | 7 + 2 | 14975 | 15107 | 6818 |  | 8289 |  |  |  |  | 6666.7 |  |  | 1319 | [6 empty] | 1188 |  | 735 | 727 |  |  | 69.7 |  | 52.3 |  | 7 | 7.1
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 33.6k | 8 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 72 |  | 40.5 | 413.1 | 0 | 0 | 0.35 | 173.859 | 27 | 0 |  | 45 | 90 | 7 + 2 | 14949 | 15060 | 6797 |  | 8264 |  |  |  |  | 6666.7 |  |  | 1111 | [6 empty] | 1000 |  | 752.5 | 744.5 |  |  | 62.1 |  | 47.7 |  | 7 | 6
0
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 32.2k | 18 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 64 |  | 36.2 | 369.24 | 0 | 0 | 0.38 | 188.7612 | 24.1 | 0 |  | 45 | 90 | 7 + 2 | 15085 | 15307 | 6909 |  | 8399 |  |  |  |  | 6666.7 |  |  | 2222 | [6 empty] | 2000 |  | 668.4 | 660.5 |  |  | 96 |  | 64.1 |  | 7.1 | 12
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 32.2k | 18 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 95.1 |  | 35.8 | 365.16 | 0 | 0 | 0.53 | 263.2722 | 35.8 | 0 |  | 45 | 90 | 7 + 2 | 14966 | 15091 | 6811 |  | 8280.6 |  |  |  |  | 6666.7 |  |  | 1250 | [6 empty] | 1125 |  | 670 | 662.3 |  |  | 61.4 |  | 47.3 |  | 7 | 6.7
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 32.2k | 15 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 69 |  | 38.9 | 396.78 | 0 | 0 | 0.38 | 188.7612 | 25.9 | 0 |  | 45 | 90 | 7 + 2 | 15034 | 15215 | 6867 |  | 8348 |  |  |  |  | 6666.7 |  |  | 1806 | [6 empty] | 1625 |  | 679.4 | 671.5 |  |  | 83.8 |  | 58.9 |  | 7.1 | 9.7
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 32.2k | 15 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 101.8 |  | 57.5 | 586.5 | 0 | 0 | 0.53 | 263.2722 | 38.3 | 0 |  | 45 | 90 | 7 + 2 | 14915 | 14999 | 6769.4 |  | 8229.8 |  |  |  |  | 6666.7 |  |  | 833.3 | [6 empty] | 750 |  | 680.3 | 672.5 |  |  | 48.3 |  | 39.5 |  | 7 | 4.5
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 32.2k | 13 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 104 |  | 58.7 | 598.74 | 0 | 0 | 0.52 | 258.3048 | 39.1 | 0 |  | 45 | 90 | 7 + 2 | 14890 | 14952 | 6748.5 |  | 8204.4 |  |  |  |  | 6666.7 |  |  | 625 | [6 empty] | 562.5 |  | 690.2 | 682.4 |  |  | 40.5 |  | 33.8 |  | 7 | 3.4
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 32.2k | 12 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 73 |  | 40 | 408 | 0 | 0 | 0.37 | 183.7938 | 26.6 | 0 |  | 45 | 90 | 7 + 2 | 14992 | 15138 | 6832 |  | 8306 |  |  |  |  | 6666.7 |  |  | 1458 | [6 empty] | 1313 |  | 695.1 | 687.2 |  |  | 73 |  | 53.6 |  | 7 | 7.9
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 32.2k | 10 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 71 |  | 40.2 | 410.04 | 0 | 0 | 0.36 | 178.8264 | 26.8 | 0 |  | 45 | 90 | 7 + 2 | 14966 | 15091 | 6811 |  | 8281 |  |  |  |  | 6666.7 |  |  | 1250 | [6 empty] | 1125 |  | 709.1 | 701.1 |  |  | 66 |  | 49.6 |  | 7 | 6.7
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 32.2k | 8 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 71 |  | 40 | 408 | 0 | 0 | 0.35 | 173.859 | 26.6 | 0 |  | 45 | 90 | 7 + 2 | 14941 | 15045 | 6790 |  | 8255 |  |  |  |  | 6666.7 |  |  | 1042 | [6 empty] | 938 |  | 726.6 | 718.6 |  |  | 58.3 |  | 44.9 |  | 7 | 5.6
[19 empty] | 0 |  | #VALUE! |  | 0 |  | 0
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 28k | 18 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 63 |  | 35.7 | 364.14 | 0 | 0 | 0.38 | 188.7612 | 23.8 | 0 |  | 45 | 90 | 7 + 2 | 15060 | 15261 | 6888 |  | 8374 |  |  |  |  | 6666.7 |  |  | 2013.9 | [6 empty] | 1813 |  | 591.5 | 583.6 |  |  | 86.1 |  | 57.7 |  | 7.1 | 10.9
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 28k | 18 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 95.5 |  | 53.8 | 548.76 | 0 | 0 | 0.53 | 263.2722 | 35.9 | 0 |  | 45 | 90 | 7 + 2 | 14932 | 15030 | 6783.4 |  | 8246.7 |  |  |  |  | 6666.7 |  |  | 972.2 | [6 empty] | 875 |  | 592.7 | 584.9 |  |  | 49.7 |  | 39.2 |  | 7 | 5.2
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 28k | 15 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 68 |  | 38.3 | 390.66 | 0 | 0 | 0.38 | 188.7612 | 25.6 | 0 |  | 45 | 90 | 7 + 2 | 15000 | 15153 | 6839 |  | 8314 |  |  |  |  | 6666.7 |  |  | 1528 | [6 empty] | 1375 |  | 602.8 | 594.9 |  |  | 70.8 |  | 50.5 |  | 7.1 | 8.2
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 28k | 15 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 102.4 |  | 38.5 | 392.7 | 0 | 0 | 0.53 | 263.2722 | 38.5 | 0 |  | 45 | 90 | 7 + 2 | 14881 | 14937 | 6741.6 |  | 8195.9 |  |  |  |  | 6666.7 |  |  | 555.6 | [6 empty] | 500 |  | 603.6 | 598.6 |  |  | 36.4 |  | 30.5 |  | 7 | 3
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 28k | 13 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 106.1 |  | 59.9 | 610.98 | 0 | 0 | 0.52 | 258.3048 | 39.9 | 0 |  | 45 | 90 | 7 + 2 | 14848 | 14875 | 6713.3 |  | 8162 |  |  |  |  | 6666.7 |  |  | 277.8 | [6 empty] | 250 |  | 613.3 | 605.5 |  |  | 25.6 |  | 21.7 |  | 6.9 | 1.5
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 28k | 12 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 71 |  | 40.2 | 410.04 | 0 | 0 | 0.38 | 188.7612 | 26.8 | 0 |  | 45 | 90 | 7 + 2 | 14949 | 15060 | 6797 |  | 8264 |  |  |  |  | 6666.7 |  |  | 1111 | [6 empty] | 1000 |  | 618.7 | 610.8 |  |  | 56.3 |  | 42.3 |  | 7
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 28k | 10 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 72 |  | 40.3 | 411.06 | 0 | 0 | 0.36 | 178.8264 | 26.9 | 0 |  | 45 | 90 | 7 + 2 | 14924 | 15014 | 6776 |  | 8238 |  |  |  |  | 6666.7 |  |  | 903 | [6 empty] | 813 |  | 632.7 | 624.7 |  |  | 48.6 |  | 37.3 |  | 7 | 4.9
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 28k | 8 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 73 |  | 41 | 418.2 | 0 | 0 | 0.36 | 178.8264 | 27.4 | 0 |  | 45 | 90 | 7 + 2 | 14980 | 14952 | 6749 |  | 8204 |  |  |  |  | 6666.7 |  |  | 625 | [6 empty] | 563 |  | 650.3 | 642.3 |  |  | 36.9 |  | 29.1 |  | 7 | 3.4
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 24k | 18 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 59.6 |  | 33.5 | 341.7 | 0 | 0 | 0.38 | 188.7612 | 22.4 | 0 |  | 45 | 90 | 7 + 2 | 15043 | 15230 | 6873.9 |  | 8356.8 |  |  |  |  | 6666.7 |  |  | 1875 | [6 empty] | 1687.5 |  | 525.6 | 517.6 |  |  | 79.2 |  | 53.1 |  | 7.1 | 10.1
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 24k | 18 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 87.4 |  | 49.2 | 501.84 | 0 | 0 | 0.53 | 263.2722 | 32.8 | 0 |  | 45 | 90 | 7 + 2 | 14920 | 15006 | 6772.9 |  | 8234 |  |  |  |  | 6666.7 |  |  | 868.1 | [6 empty] | 781.3 |  | 526.3 | 518.5 |  |  | 43.5 |  | 34 |  | 7 | 4.7
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 24k | 15 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 64 |  | 36.1 | 368.22 | 0 | 0 | 0.38 | 188.7612 | 24.1 | 0 |  | 45 | 90 | 7 + 2 | 14983 | 15122 | 6825.2 |  | 8298 |  |  |  |  | 6666.7 |  |  | 1389 | [6 empty] | 1250 |  | 537 | 529.3 |  |  | 63.6 |  | 45.3 |  | 7 | 7.5
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 24k | 15 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 94.5 |  | 53.2 | 542.64 | 0 | 0 | 0.53 | 263.2722 | 35.45 | 0 |  | 46 | 90 | 7 + 2 | 14865 | 14906 | 6727.7 |  | 8179 |  |  |  |  | 6666.7 |  |  | 416.7 | [6 empty] | 375 |  | 537.6 | 529.8 |  |  | 29.4 |  | 24.6 |  | 6.9 | 2.2
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 24k | 15 | 7 | 1 | 497 | 27 | 12 | 8 | 10.5 | 98.3 |  | 55.3 | 564.06 | 0 | 0 | 0.52 | 258.3048 | 35.6 | 0 |  | 45 | 90 | 7 + 2 | 14856 | 14891 | 6720.7 |  | 8170.5 |  |  |  |  | 6666.7 |  |  | 347.2 | [6 empty] | 312.5 |  | 537.6 | 529.8 |  |  | 38.7 |  | 31 |  | 6.9 | 3.7
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 24k | 13 | 7 | "2/1" | wont converge
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 24k | 12 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 68 |  | 38.4 | 391.68 | 0 | 0 | 0.38 | 188.7612 | 25.6 | 0 |  | 45 | 90 | 7 + 2 | 14924 | 15014 | 6776 |  | 8238 |  |  |  |  | 6666.7 |  |  | 903 | [6 empty] | 813 |  | 553.5 | 545.5 |  |  | 45.9 |  | 34.7 |  | 7 | 4.9
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 24k | 10 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 70 |  | 39.1 | 398.82 | 0 | 0 | 0.38 | 188.7612 | 26.1 | 0 |  | 45 | 90 | 7 + 2 | 14890 | 14952 | 6749 |  | 8204 |  |  |  |  | 6666.7 |  |  | 625 | [6 empty] | 562 |  | 567.4 | 559.4 |  |  | 34.8 |  | 27.1 |  | 7 | 3.4
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 24k | 8 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 71 |  | 40 | 408 | 0 | 0 | 0.37 | 183.7938 | 26.6 | 0 |  | 45 | 90 | 7 + 2 | 14856 | 14891 | 6721 |  | 8171 |  |  |  |  | 6666.7 |  |  | 347 | [6 empty] | 313 |  | 584.6 | 576.5 |  |  | 22.8 |  | 18 |  | 6.9 | 1.9
[5 empty] | 9.6 SWC5LD ESPA2MAX | 0 | 24k | 8 | 7 | 1 | 497 | 27 | 12 | 8 | 10.5 | 72 |  | 40.4 | 412.08 | 0 | 0 | 0.37 | 183.7938 | 27 | 0 |  | 45 | 90 | 7 + 1 | 14848 | 14875 | 6713.7 |  | 8162 |  |  |  |  | 6666.7 |  |  | 277.8 | [6 empty] | 250 |  | 584.5 | 576.5 |  |  | 32.5 |  | 25.4 |  | 6.9 | 3
96.4
MOTOR DATA
kW | EFF | HP
OUTPUT | 100% | OUTPUT
0 | 84.5 | 0
0.37 | 84.5 | 0.49333
0.55 | 84.5 | 0.73333
0.75 | 84.5 | 1
1.1 | 85.9 | 1.4667
1.5 | 87 | 2
2.2 | 88.2 | 2.9333
3 | 89.1 | 4
4 | 89.9 | 5.3333
5.5 | 90.7 | 7.3333
7.5 | 91.5 | 10
11 | 92.2 | 14.6667
15 | 92.9 | 20
18.5 | 93.3 | 24.6667
22 | 93.6 | 29.3333
30 | 94.2 | 40
37 | 94.5 | 49.3333
45 | 94.8 | 60
55 | 95 | 73.3333
75 | 95.5 | 100
90 | 95.7 | 120
110 | 96 | 146.6667
132 | 96.1 | 176
150 | 96.3 | 200
185 | 96.3 | 246.6667
200 | 96.3 | 266.6667
220 | 96.3 | 293.3333
260 | 96.3 | 346.6667
280 | 96.3 | 373.3333
315 | 96.3 | 420
355 | 96.3 | 473.3333
400 | 96.3 | 533.3333
450 | 96.4 | 600
540 | 96.5 | 720
575 | 96.5 | 766.6667
610 | 96.5 | 813.3333
1350 | 96.5 | 1800
4500 | 96.5 | 6000
Note on C7: Steven Alt: 10 psi min for DWEERS. Pump NPSHR is 16 meters. Use 20 psig to be safe minus 5 psi feed tank + Cartridge filter dP 3 psi (commissioning, 8 psi 3 - 5 years)
Note on C16: Steven Alt: Projected pressure minus incoming + 1 psi line loss + 10 psi destination
Note on C25: Steven Alt: Equals Membrane dp (commissioning, 50% more 3.5 years) + 5 psi line losses + DWEER Loss (97.5% efficient
Note on C34: Steven Alt: Projected pressure minus 5 psi tank head + 1 psi line loss + 10 psi product water tank head
Note on C43: Steven Alt: Per RFP, 305 feet plus plant piping and valve losses ( 2 psi)
Note on C46: Steven Alt: 80% 400 HPs, 75% smaller
Note on C51: Steven Alt: This based upon projected pressures with safety factors for quality but not for pressure!
Note on U54: Steven Alt: For TDS less than average, both bromide and chloride drop in the same proportion, so ok to keep /21000*71
Note that:
1. Design is fully capable of meeting Maximum Average Water Quality for temperatures between 8 and 20 (see values struck out)
2. Hydranautics has waived the 2nd pass RO requirements for minimum brine flow as long as the beta (concentration polarization) is less than 1.4 (All are). It may be beneficial to run only 1 second pass RO train at some conditions-but energy between running 1 or 2 trains is roughly the same

## RO Projections
[15 empty] | Br to Cl psg | 1.3
Targets
[13 empty] | Avg | Not Exc | Avg | Not Exc | Avg | Not Exc | Avg | Not Exc
[13 empty] | 60 | 100 | 0.3 | 0.5 | 0.5 | 0.7 | 35 | 60 |  |  |  |  | FLOW, gpm | [19 empty] | PRESSURE, psig | [8 empty] | FLUX, GFD
[13 empty] | Projected/Warranted Water Quality | [11 empty] | 1st pass | [8 empty] | total | CIP | 2nd pass | 2nd pass | [7 empty] | 1st pass |  |  |  | 2nd pass |  |  |  |  | 1st pass | 2nd pass
DESIGN - TRAIN | years | TDS | temp | racks |  | Per Train PV |  |  | PH |  | TDS |  | Chloride |  | Bromide |  | Boron |  | Sodium |  | Recovery (%) |  |  | # Trains in | TOTAL inlet to RO | inlet | inlet | per hp pump | ERD Recic | per ERD | brine to pumps | per ERD pump | brine to ERD | total | front permeate | CIP | inlet | inlet | 1st permeate | 1st brine | 2st permeate | 2ns pass Brine | 2st brine per train | permeate | permeate | inlet | brine | front | rear | inlet | 1st permeate | Brine | 2nd permeate
ref |  | mg/l | degC | 1st | 2nd | 1st pass | 1st stg | 2nd stg | 1st | 2nd | mg/l |  | Proj mg/L | War mg/L | Proj mg/L | War mg/L | Proj mg/L | War mg/L | Proj mg/L | War mg/L | total | 1st | 2nd | Operation | - BRINE 2nd pass | membranes | to HPP |  | pump | (pump) |  |  |  | permeate |  |  |  | per 2ND pass
Hydranautics | [7 empty] | O yr safety factors |  |  |  | 1.3 | 34 | 1.3 |  | 1.3 | 0.38 | 1.3 | 26.5 | 1.3
[8 empty] | 3- 5 year safety factors |  |  |  | 1.5 | 29 | 1.5 |  | 1.5 | 0.33 | 1.5 | 23 | 1.5
9.6 SWC5LD ESPA2MAX | 5 | Max | 20 | 6 | 2 | 426 | 54 | 24 | 8.3 | 10.2 | 86.3 |  | 48.4 | 72.6 | 0.32958 | 0.49437 | 0.43 | 0.645 | 32.2 | 48.3 |  | 45 | 90 | 6 + 2 | 15043 | 15230 | 6873.9 |  | 8356.8 |  |  |  |  | 6666.7 |  |  | 1875 | [6 empty] | 1687.5 |  | 849.8 | 839.9 |  |  | 88.6 |  | 63 |  | 8.3 | 10.1
9.6 SWC5LD ESPA2MAX | 5 | Max | 8 | 6 | 2 | 426 | 54 | 24 | 8.3 | 10.2 | 85.8 |  | 48 | 72 | 0.32686 | 0.49029 | 0.35 | 0.525 | 32.1 | 48.15 |  | 45 | 90 | 6 + 2 | 14890 | 14952 | 6748.5 |  | 8204.4 |  |  |  |  | 6666.7 |  |  | 625 | [6 empty] | 563 |  | 968.7 | 958.7 |  |  | 42 |  | 34.1 |  | 8.1 | 3.4
9.6 SWC5LD ESPA2MAX | 3.5 | Max | 20 | 6 | 2 | 426 | 54 | 24 | 8.3 | 10.2 | 87 |  | 48.7 | 73.05 | 0.33162 | 0.49744 | 0.44 | 0.66 | 32.4 | 48.6 |  | 45 | 90 | 6 + 2 | 15034 | 15215 | 6867 |  | 8348 |  |  |  |  | 6666.7 |  |  | 1805.6 | [6 empty] | 1625 |  | 833.8 | 823.9 |  |  | 83.4 |  | 59.6 |  | 8.3 | 9.7
9.6 SWC5LD ESPA2MAX | 3.5 | Max | 8 | 6 | 2 | 426 | 54 | 24 | 8.3 | 10.2 | 87.6 |  | 49.1 | 73.65 | 0.33435 | 0.50152 | 0.35 | 0.525 | 32.8 | 49.2 |  | 45 | 90 | 6 + 2 | 14881 | 14937 | 6741.6 |  | 8195.9 |  |  |  |  | 6666.7 |  |  | 555.6 | [6 empty] | 500 |  | 940.2 | 930.3 |  |  | 37.5 |  | 30.6 |  | 8.1 | 3
9.6 SWC5LD ESPA2MAX | 5 | Avg | 20 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 79.6 |  | 44.9 | 67.35 | 0.21778 | 0.32666 | 0.46 | 0.69 | 30 | 45 |  | 45 | 90 | 6 + 2 | 15043 | 15230 | 6873.9 |  | 8356.8 |  |  |  |  | 6666.7 |  |  | 1875 | [6 empty] | 1687.5 |  | 774.4 | 764.4 |  |  | 87 |  | 61.1 |  | 8.3 | 10.1
9.6 SWC5LD ESPA2MAX | 5 | Avg | 18 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 84 |  | 47.4 | 71.1 | 0.2299 | 0.34485 | 0.46 | 0.69 | 31.6 | 47.4 |  | 45 | 90 | 6 + 2 | 15000 | 15135 | 6839.1 |  | 8314.4 |  |  |  |  | 6666.7 |  |  | 1527.8 | [6 empty] | 1375 |  | 785.3 | 775.3 |  |  | 75.1 |  | 55 |  | 8.2 | 8.2
9.6 SWC5LD ESPA2MAX | 5 | Avg | 15 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 89 |  | 50.2 | 75.3 | 0.24348 | 0.36522 | 0.46 | 0.69 | 33.5 | 50.25 |  | 45 | 90 | 6 + 2 | 14941 | 15045 | 6790.3 |  | 8255.2 |  |  |  |  | 6666.7 |  |  | 1041.7 | [6 empty] | 937.5 |  | 806.5 | 796.6 |  |  | 57 |  | 44.1 |  | 8.2 | 5.6
9.6 SWC5LD ESPA2MAX | 5 | Avg | 13 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 91.7 |  | 51.7 | 77.55 | 0.25076 | 0.37614 | 0.46 | 0.69 | 34.5 | 51.75 |  | 45 | 90 | 6 + 2 | 14907 | 14983 | 6762.5 |  | 8221.3 |  |  |  |  | 6666.7 |  |  | 763.9 | [6 empty] | 687.5 |  | 824.8 | 814.8 |  |  | 45.3 |  | 36.1 |  | 8.1 | 4.1
9.6 SWC5LD ESPA2MAX | 5 | Avg | 12 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 62 |  | 34.9 | 52.35 | 0.16927 | 0.25391 | 0.32 | 0.48 | 23.3 | 34.95 |  | 45 | 90 | 6 + 2 | 15030 | 15207 | 6863.5 |  | 8344.1 |  |  |  |  | 6666.7 |  |  | 1770.8 | [6 empty] | 1593.8 |  | 835.7 | 825.5 |  |  | 96.6 |  | 70.9 |  | 8.3 | 9.6
9.6 SWC5LD ESPA2MAX | 5 | Avg | 10 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 61.7 |  | 34.8 | 52.2 | 0.16879 | 0.25318 | 0.31 | 0.465 | 23.2 | 34.8 |  | 45 | 90 | 6 + 2 | 15005 | 15161 | 6842.6 |  | 8318.7 |  |  |  |  | 6666.7 |  |  | 1562.5 | [6 empty] | 1406.3 |  | 860.7 | 850.5 |  |  | 89.8 |  | 67.5 |  | 8.2 | 8.4
9.6 SWC5LD ESPA2MAX | 5 | Avg | 8 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 61.5 |  | 34.7 | 52.05 | 0.1683 | 0.25245 | 0.3 | 0.45 | 23.2 | 34.8 |  | 45 | 90 | 6 + 2 | 14975 | 15107 | 6818.2 |  | 8289 |  |  |  |  | 6666.7 |  |  | 1319.4 | [6 empty] | 1187.5 |  | 891 | 880.7 |  |  | 80.2 |  | 61.9 |  | 8.2 | 7.1
9.6 SWC5LD ESPA2MAX | 3.5 | Avg | 20 | 6 | 2 | 426 | 54 | 24 | 8 | 10.4 | 51.4 |  | 29 | 43.5 | 0.14066 | 0.21099 | 0.33 | 0.495 | 19.3 | 28.95 |  | 45 | 90 | 6 + 2 | 15187 | 15493 | 6992.3 |  | 8500.7 |  |  |  |  | 6666.7 |  |  | 3055.6 | [6 empty] | 2750 |  | 757.6 | 747.4 |  |  | 132.9 |  | 83.1 |  | 8.4 | 16.5
9.6 SWC5LD ESPA2MAX | 3.5 | Avg | 20 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 80.2 |  | 45.2 | 67.8 | 0.21923 | 0.32885 | 0.46 | 0.69 | 30.1 | 45.15 |  | 45 | 90 | 6 + 2 | 15034 | 15215 | 6866.9 |  | 8348.3 |  |  |  |  | 6666.7 |  |  | 1805.6 | [6 empty] | 1625 |  | 759.3 | 749.5 |  |  | 81.8 |  | 57.5 |  | 8.3 | 9.7
9.6 SWC5LD ESPA2MAX | 3.5 | Avg | 18 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 56.7 |  | 32 | 48 | 0.15521 | 0.23281 | 0.33 | 0.495 | 21.3 | 31.95 |  | 45 | 90 | 6 + 2 | 15128 | 15385 | 6943.6 |  | 8441.4 |  |  |  |  | 6666.7 |  |  | 2569.4 | [6 empty] | 2312.5 |  | 768.1 | 758 |  |  | 117.1 |  | 77.1 |  | 8.4 | 13.9
9.6 SWC5LD ESPA2MAX | 3.5 | Avg | 18 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 82.6 |  | 46.6 | 69.9 | 0.22602 | 0.33903 | 0.46 | 0.69 | 31.1 | 46.65 |  | 45 | 90 | 6 + 2 | 15000 | 15153 | 6839.1 |  | 8314.1 |  |  |  |  | 6666.7 |  |  | 1527.8 | [6 empty] | 1375 |  | 769 | 759.1 |  |  | 73 |  | 53.1 |  | 8.2 | 8.2
9.6 SWC5LD ESPA2MAX | 3.5 | Avg | 16 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 59 |  | 33.3 | 49.95 | 0.16151 | 0.24227 | 0.33 | 0.495 | 22.2 | 33.3 |  | 45 | 90 | 6 + 2 | 15094 | 15323 | 6915.7 |  | 8408 |  |  |  |  | 6666.7 |  |  | 2291.7 | [6 empty] | 2062.5 |  | 780.3 | 770.2 |  |  | 109.4 |  | 74.5 |  | 8.3 | 12.4
9.6 SWC5LD ESPA2MAX | 3.5 | Avg | 15 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 88.3 |  | 49.8 | 74.7 | 0.24154 | 0.36231 | 0.46 | 0.69 | 33.3 | 49.95 |  | 45 | 90 | 6 + 2 | 14941 | 15045 | 6790.3 |  | 8255.2 |  |  |  |  | 6666.7 |  |  | 1041.7 | [6 empty] | 937.5 |  | 788 | 778.1 |  |  | 55.5 |  | 42.8 |  | 8.2 | 5.6
9.6 SWC5LD ESPA2MAX | 3.5 | Avg | 14 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 60.5 |  | 34.1 | 51.15 | 0.16539 | 0.24809 | 0.33 | 0.495 | 22.8 | 34.2 |  | 45 | 90 | 6 + 2 | 15060 | 15261 | 6888 |  | 8374 |  |  |  |  | 6666.7 |  |  | 2013.9 | [6 empty] | 1812.5 |  | 795.4 | 785.3 |  |  | 100.9 |  | 71.1 |  | 8.3 | 10.9
9.6 SWC5LD ESPA2MAX | 3.5 | Avg | 13 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 91.2 |  | 51.5 | 77.25 | 0.24979 | 0.37468 | 0.46 | 0.69 | 34.4 | 51.6 |  | 45 | 90 | 6 + 2 | 14907 | 14983 | 6762.5 |  | 8221.3 |  |  |  |  | 6666.7 |  |  | 763.9 | [6 empty] | 687.5 |  | 804.4 | 794.5 |  |  | 44.3 |  | 35.2 |  | 8.1 | 4.1
9.6 SWC5LD ESPA2MAX | 3.5 | Avg | 12 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 61.9 |  | 34.9 | 52.35 | 0.16927 | 0.25391 | 0.32 | 0.48 | 23.3 | 34.95 |  | 45 | 90 | 6 + 2 | 15026 | 15199 | 6860 |  | 8340 |  |  |  |  | 6666.7 |  |  | 1736.1 | [6 empty] | 1562.5 |  | 814 | 803.8 |  |  | 91.6 |  | 66.6 |  | 8.2 | 9.4
9.6 SWC5LD ESPA2MAX | 3.5 | Avg | 10 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 61.8 |  | 34.9 | 52.35 | 0.16927 | 0.25391 | 0.31 | 0.465 | 23.3 | 34.95 |  | 45 | 90 | 6 + 2 | 15000 | 15153 | 6839.1 |  | 8314.4 |  |  |  |  | 6666.7 |  |  | 1527.8 | [6 empty] | 1375 |  | 836.6 | 826.5 |  |  | 84.8 |  | 63.3 |  | 8.2 | 8.2
9.6 SWC5LD ESPA2MAX | 3.5 | Avg | 8 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 62.4 |  | 35.2 | 52.8 | 0.17073 | 0.25609 | 0.3 | 0.45 | 23.4 | 35.1 |  | 45 | 90 | 6 + 2 | 14966 | 15091 | 6811.2 |  | 8280.6 |  |  |  |  | 6666.7 |  |  | 1250 | [6 empty] | 1125 |  | 864.1 | 854 |  |  | 73.5 |  | 56.5 |  | 8.2 | 6.7
9.6 SWC5LD ESPA2MAX | 5 | 33.6 | 12 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 62.1 |  | 35 | 52.5 | 0.16976 | 0.25464 | 0.32 | 0.48 | 23.4 | 35.1 |  | 45 | 90 | 6 + 2 | 15022 | 15192 | 6856.5 |  | 8335.6 |  |  |  |  | 6666.7 |  |  | 1701.4 | [6 empty] | 1531.3 |  | 819.7 | 809.5 |  |  | 92.8 |  | 68.3 |  | 8.3 | 9.2
9.6 SWC5LD ESPA2MAX | 3.5 | 33.6 | 12 | 6 | 2 | 426 | 54 | 24 | 8 | 10.5 | 62.1 |  | 35 | 52.5 | 0.16976 | 0.25464 | 0.32 | 0.48 | 23.4 | 35.1 |  | 45 | 90 | 6 + 2 | 15017 | 15184 | 6853 |  | 8331 |  |  |  |  | 6666.7 |  |  | 1667 | [6 empty] | 1500 |  | 797.6 | 787.5 |  |  | 87.8 |  | 64.1 |  | 8.2 | 9
9.6 SWC5LD ESPA2MAX | 0 | Max | 18 | 7 | 2 | 497 | 54 | 24 | 8.3 | 10.2 |  |  | 56 | 72.8 | 0.38133 | 0.49573 | 0.49 | 0.637 | 40.7 | 52.91 |  | 45 | 90 | 7 + 2 | 14992 | 15138 | 6832.1 |  | 8306 |  |  |  |  | 6666.7 |  |  | 1458.3 | [6 empty] | 1312.5 |  | 780.6 | 773 |  |  | 73.3 |  | 57.6 |  | 7 | 7.9
9.6 SWC5LD ESPA2MAX | 0 | Max | 15 | 7 | 2 | 497 | 54 | 24 | 8.3 | 10.2 | 101.5 |  | 57 | 74.1 | 0.38814 | 0.50459 | 0.47 | 0.611 | 37.9 | 49.27 |  | 45 | 90 | 7 + 2 | 14958 | 15076 | 6904 |  | 8272 |  |  |  |  | 6666.7 |  |  | 1180.6 | [6 empty] | 1063 |  | 793.8 | 786.1 |  |  | 65.5 |  | 50.2 |  | 7 | 6.4
9.6 SWC5LD ESPA2MAX | 0 | Max | 12 | 7 | 2 | 497 | 54 | 24 | 8.3 | 10.2 | 99.4 |  | 56 | 72.8 | 0.38133 | 0.49573 | 0.43 | 0.559 | 37.2 | 48.36 |  | 45 | 90 | 7 + 2 | 14932 | 15030 | 6783.4 |  | 8247 |  |  |  |  | 6666.7 |  |  | 972 | [6 empty] | 875 |  | 809.3 | 801.6 |  |  | 55.9 |  | 44.9 |  | 7 | 5.2
9.6 SWC5LD ESPA2MAX | 0 | Max | 10 | 7 | 2 | 497 | 54 | 24 | 8.3 | 10.2 | 101 |  | 56 | 72.8 | 0.38133 | 0.49573 | 0.42 | 0.546 | 37.6 | 48.88 |  | 45 | 90 | 7 + 2 | 14907 | 14983 | 6762.5 |  | 8221 |  |  |  |  | 6666.7 |  |  | 764 | [6 empty] | 688 |  | 823.2 | 815.4 |  |  | 47.8 |  | 39.2 |  | 7 | 4.1
9.6 SWC5LD ESPA2MAX | 0 | Max | 8 | 7 | 2 | 497 | 54 | 24 | 8.3 | 10.2 | 101 |  | 57 | 74.1 | 0.38814 | 0.50459 | 0.41 | 0.533 | 37.9 | 49.27 |  | 45 | 90 | 7 + 2 | 14881 | 14937 | 6741.6 |  | 8196 |  |  |  |  | 6666.7 |  |  | 556 | [6 empty] | 500 |  | 840.9 | 833 |  |  | 39.1 |  | 32.7 |  | 7 | 3
9.6 SWC5LD ESPA2MAX | 0 | Avg | 18 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 65 |  | 36.4 | 47.32 | 0.17655 | 0.22951 | 0.38 | 0.494 | 24.3 | 31.59 |  | 45 | 90 | 7 + 2 | 15102 | 15338 | 6922.7 |  | 8416 |  |  |  |  | 6666.7 |  |  | 2361 | [6 empty] | 2125 |  | 711 | 703 |  |  | 102 |  | 68 |  | 7.1 | 12.7
9.6 SWC5LD ESPA2MAX | 0 | Avg | 18 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 94.8 |  | 53.6 | 69.68 | 0.25997 | 0.33796 | 0.53 | 0.689 | 35.6 | 46.28 |  | 56 | 90 | 7 + 2 | 14983 | 15122 | 6825.2 |  | 8297.5 |  |  |  |  | 6666.7 |  |  | 1388.9 | [6 empty] | 1250 |  | 712.9 | 705.2 |  |  | 67.5 |  | 51.4 |  | 7 | 7.5
9.6 SWC5LD ESPA2MAX | 0 | Avg | 15 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 69 |  | 39 | 50.7 | 0.18916 | 0.24591 | 0.38 | 0.494 | 26 | 33.8 |  | 45 | 90 | 7 + 2 | 15051 | 15246 | 6880.9 |  | 8365.2 |  |  |  |  | 6666.7 |  |  | 1944 | [6 empty] | 1750 |  | 721.8 | 713.9 |  |  | 90.4 |  | 63.1 |  | 7.1 | 10.5
9.6 SWC5LD ESPA2MAX | 0 | Avg | 15 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 102.4 |  | 57.8 | 75.14 | 0.28034 | 0.36445 | 0.53 | 0.689 | 38.5 | 50.05 |  | 45 | 90 | 7 + 2 | 14932 | 15030 | 6783.4 |  | 8246.7 |  |  |  |  | 6666.7 |  |  | 972.2 | [6 empty] | 875 |  | 723.3 | 715.6 |  |  | 54 |  | 43.5 |  | 7 | 5.2
9.6 SWC5LD ESPA2MAX | 0 | Avg | 13 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 103.6 |  | 58.5 | 76.05 | 0.28374 | 0.36886 | 0.52 | 0.676 | 39 | 50.7 |  | 45 | 90 | 7 + 2 | 14907 | 14983 | 6762.5 |  | 8221.4 |  |  |  |  | 6666.7 |  |  | 763.9 | [6 empty] | 687.5 |  | 732.8 | 725 |  |  | 46.7 |  | 38.5 |  | 7 | 4.1
9.6 SWC5LD ESPA2MAX | 0 | Avg | 13 | 7 | 1 | 497 | 27 | 12 | 8 | 10.5 | 109 |  | 61.5 | 79.95 | 0.29829 | 0.38778 | 0.53 | 0.689 | 41.1 | 53.43 |  | 45 | 90 | 7 + 1 | 14886 | 14945 | 6745.1 |  | 8200.1 |  |  |  |  | 6666.7 |  |  | 590.3 | [6 empty] | 531.3 |  | 733 | 725.3 |  |  | 64.3 |  | 50.4 |  | 7 | 6.4
9.6 SWC5LD ESPA2MAX | 0 | Avg | 12 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 72 |  | 40.5 | 52.65 | 0.19643 | 0.25536 | 0.37 | 0.481 | 27 | 35.1 |  | 45 | 90 | 7 + 2 | 15005 | 15161 | 6843 | #REF! | 8319 | #REF! | #REF! | #REF! | #REF! | 6667.1 | #REF! | #REF! | 1559 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1403 | #REF! | 737.6 | 729.7 | #REF! | #REF! | 78.4 | #REF! | 57 | #REF! | 7.1 | 8.4
9.6 SWC5LD ESPA2MAX | 0 | Avg | 10 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 72 |  | 40.5 | 52.65 | 0.19643 | 0.25536 | 0.36 | 0.468 | 27 | 35.1 |  | 45 | 90 | 7 + 2 | 14983 | 15122 | 6825 |  | 8298 |  |  |  |  | 6666.7 |  |  | 1389 | [6 empty] | 1250 |  | 751.6 | 743.6 |  |  | 73.2 |  | 54.7 |  | 7 | 7.5
9.6 SWC5LD ESPA2MAX | 0 | Avg | 8 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 72 |  | 40.5 | 52.65 | 0.19643 | 0.25536 | 0.35 | 0.455 | 27 | 35.1 |  | 45 | 90 | 7 + 2 | 14958 | 15076 | 6804 |  | 8272 |  |  |  |  | 6666.7 |  |  | 1180.6 | [6 empty] | 1063 |  | 769.2 | 761.2 |  |  | 66 |  | 50 |  | 7 | 6.4
[14 empty] | 0 |  |  |  | 0 |  | 0
9.6 SWC5LD ESPA2MAX | 0 | 33.6k | 18 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 65 |  | 36.5 | 47.45 | 0.17703 | 0.23014 | 0.38 | 0.494 | 24.3 | 31.59 |  | 45 | 90 | 7 + 2 | 15094 | 15323 | 6916 |  | 8408 |  |  |  |  | 6666.7 |  |  | 2292 | [6 empty] | 2063 |  | 694.4 | 686.6 |  |  | 99.2 |  | 66.1 |  | 7.1 | 12.4
9.6 SWC5LD ESPA2MAX | 0 | 33.6k | 18 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 95.2 |  | 53.8 | 69.94 | 0.26094 | 0.33923 | 0.53 | 0.689 | 35.8 | 46.54 |  | 45 | 90 | 7 + 2 | 14975 | 15107 | 6818.2 |  | 8289 |  |  |  |  | 6666.7 |  |  | 1319.4 | [6 empty] | 1187.5 |  | 696.2 | 688.5 |  |  | 64.8 |  | 49.7 |  | 7 | 7.1
9.6 SWC5LD ESPA2MAX | 0 | 33.6k | 18 | 7 | 1 | 497 | 27 | 12 | 8 | 10.5 | 99.3 |  | 56 | 72.8 | 0.27161 | 0.3531 | 0.53 | 0.689 | 37.4 | 48.62 |  | 45 | 90 | 7 + 1 | 14964 | 15068 | 6800.8 |  | 8267.9 |  |  |  |  | 6666.7 |  |  | 1145.8 | [6 empty] | 1031.3 |  | 696.5 | 688.8 |  |  | 103.7 |  | 71.8 |  | 7 | 12.4
9.6 SWC5LD ESPA2MAX | 0 | 33.6k | 15 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 70 |  | 39.2 | 50.96 | 0.19013 | 0.24717 | 0.38 | 0.494 | 26.1 | 33.93 |  | 45 | 90 | 7 + 2 | 15043 | 15230 | 6874 |  | 8357 |  |  |  |  | 6666.7 |  |  | 1875 | [6 empty] | 1688 |  | 705.2 | 697.3 |  |  | 87.2 |  | 61.1 |  | 7.1 | 10.1
9.6 SWC5LD ESPA2MAX | 0 | 33.6k | 15 | 7 | 1 | 497 | 27 | 12 | 8 | 10.5 | 105.4 |  | 59.5 | 77.35 | 0.28859 | 0.37517 | 0.53 |  | 39.7 | 51.61 |  | 45 | 90 | 7 + 1 | 14907 | 14983 | 6762.5 |  | 8221.3 |  |  |  |  | 6666.7 |  |  | 763.9 | [6 empty] | 687.5 |  | 706.8 | 699.1 |  |  | 77 |  | 58.1 |  | 7 | 8.2
9.6 SWC5LD ESPA2MAX | 0 | 33.6k | 13 | 7 | 1 | 497 | 27 | 12 | 8 | 10.5 | 108.2 |  | 61 | 79.3 | 0.29586 | 0.38462 | 0.53 | 0.689 | 40.7 | 52.91 |  | 45 | 90 | 7 + 1 | 14881 | 14937 | 6741.6 |  | 8195.9 |  |  |  |  | 6666.7 |  |  | 555.6 | [6 empty] | 500 |  | 716.4 | 708.6 |  |  | 60.9 |  | 48 |  | 7 | 6
9.6 SWC5LD ESPA2MAX | 0 | 33.6k | 12 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 71 |  | 40.2 | 52.26 | 0.19498 | 0.25347 | 0.37 | 0.481 | 26.8 | 34.84 |  | 45 | 90 | 7 + 2 | 15000 | 15153 | 6839.1 |  | 8314 |  |  |  |  | 6666.7 |  |  | 1528 | [6 empty] | 1375 |  | 721 | 713 |  |  | 76.6 |  | 56.1 |  | 7.1 | 8.2
9.6 SWC5LD ESPA2MAX | 0 | 33.6k | 10 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 72 |  | 40.7 | 52.91 | 0.1974 | 0.25663 | 0.36 | 0.468 | 27.1 | 35.23 |  | 45 | 90 | 7 + 2 | 14975 | 15107 | 6818 |  | 8289 |  |  |  |  | 6666.7 |  |  | 1319 | [6 empty] | 1188 |  | 735 | 727 |  |  | 69.7 |  | 52.3 |  | 7 | 7.1
9.6 SWC5LD ESPA2MAX | 0 | 33.6k | 8 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 72 |  | 40.5 | 52.65 | 0.19643 | 0.25536 | 0.35 | 0.455 | 27 | 35.1 |  | 45 | 90 | 7 + 2 | 14949 | 15060 | 6797 |  | 8264 |  |  |  |  | 6666.7 |  |  | 1111 | [6 empty] | 1000 |  | 752.5 | 744.5 |  |  | 62.1 |  | 47.7 |  | 7 | 6
0
9.6 SWC5LD ESPA2MAX | 0 | 32.2k | 18 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 64 |  | 36.2 | 47.06 | 0.17558 | 0.22825 | 0.38 | 0.494 | 24.1 | 31.33 |  | 45 | 90 | 7 + 2 | 15085 | 15307 | 6909 |  | 8399 |  |  |  |  | 6666.7 |  |  | 2222 | [6 empty] | 2000 |  | 668.4 | 660.5 |  |  | 96 |  | 64.1 |  | 7.1 | 12
9.6 SWC5LD ESPA2MAX | 0 | 32.2k | 18 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 95.1 |  | 35.8 | 46.54 | 0.17364 | 0.22573 | 0.53 | 0.689 | 35.8 | 46.54 |  | 45 | 90 | 7 + 2 | 14966 | 15091 | 6811 |  | 8280.6 |  |  |  |  | 6666.7 |  |  | 1250 | [6 empty] | 1125 |  | 670 | 662.3 |  |  | 61.4 |  | 47.3 |  | 7 | 6.7
9.6 SWC5LD ESPA2MAX | 0 | 32.2k | 15 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 69 |  | 38.9 | 50.57 | 0.18867 | 0.24528 | 0.38 | 0.494 | 25.9 | 33.67 |  | 45 | 90 | 7 + 2 | 15034 | 15215 | 6867 |  | 8348 |  |  |  |  | 6666.7 |  |  | 1806 | [6 empty] | 1625 |  | 679.4 | 671.5 |  |  | 83.8 |  | 58.9 |  | 7.1 | 9.7
9.6 SWC5LD ESPA2MAX | 0 | 32.2k | 15 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 101.8 |  | 57.5 | 74.75 | 0.27889 | 0.36256 | 0.53 | 0.689 | 38.3 | 49.79 |  | 45 | 90 | 7 + 2 | 14915 | 14999 | 6769.4 |  | 8229.8 |  |  |  |  | 6666.7 |  |  | 833.3 | [6 empty] | 750 |  | 680.3 | 672.5 |  |  | 48.3 |  | 39.5 |  | 7 | 4.5
9.6 SWC5LD ESPA2MAX | 0 | 32.2k | 13 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 104 |  | 58.7 | 76.31 | 0.28471 | 0.37012 | 0.52 | 0.676 | 39.1 | 50.83 |  | 45 | 90 | 7 + 2 | 14890 | 14952 | 6748.5 |  | 8204.4 |  |  |  |  | 6666.7 |  |  | 625 | [6 empty] | 562.5 |  | 690.2 | 682.4 |  |  | 40.5 |  | 33.8 |  | 7 | 3.4
9.6 SWC5LD ESPA2MAX | 0 | 32.2k | 12 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 73 |  | 40 | 52 | 0.19401 | 0.25221 | 0.37 | 0.481 | 26.6 | 34.58 |  | 45 | 90 | 7 + 2 | 14992 | 15138 | 6832 |  | 8306 |  |  |  |  | 6666.7 |  |  | 1458 | [6 empty] | 1313 |  | 695.1 | 687.2 |  |  | 73 |  | 53.6 |  | 7 | 7.9
9.6 SWC5LD ESPA2MAX | 0 | 32.2k | 10 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 71 |  | 40.2 | 52.26 | 0.19498 | 0.25347 | 0.36 | 0.468 | 26.8 | 34.84 |  | 45 | 90 | 7 + 2 | 14966 | 15091 | 6811 |  | 8281 |  |  |  |  | 6666.7 |  |  | 1250 | [6 empty] | 1125 |  | 709.1 | 701.1 |  |  | 66 |  | 49.6 |  | 7 | 6.7
9.6 SWC5LD ESPA2MAX | 0 | 32.2k | 8 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 71 |  | 40 | 52 | 0.19401 | 0.25221 | 0.35 | 0.455 | 26.6 | 34.58 |  | 45 | 90 | 7 + 2 | 14941 | 15045 | 6790 |  | 8255 |  |  |  |  | 6666.7 |  |  | 1042 | [6 empty] | 938 |  | 726.6 | 718.6 |  |  | 58.3 |  | 44.9 |  | 7 | 5.6
[14 empty] | 0 |  |  |  | 0 |  | 0
9.6 SWC5LD ESPA2MAX | 0 | 28k | 18 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 63 |  | 35.7 | 46.41 | 0.17315 | 0.2251 | 0.38 | 0.494 | 23.8 | 30.94 |  | 45 | 90 | 7 + 2 | 15060 | 15261 | 6888 |  | 8374 |  |  |  |  | 6666.7 |  |  | 2013.9 | [6 empty] | 1813 |  | 591.5 | 583.6 |  |  | 86.1 |  | 57.7 |  | 7.1 | 10.9
9.6 SWC5LD ESPA2MAX | 0 | 28k | 18 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 95.5 |  | 53.8 | 69.94 | 0.26094 | 0.33923 | 0.53 | 0.689 | 35.9 | 46.67 |  | 45 | 90 | 7 + 2 | 14932 | 15030 | 6783.4 |  | 8246.7 |  |  |  |  | 6666.7 |  |  | 972.2 | [6 empty] | 875 |  | 592.7 | 584.9 |  |  | 49.7 |  | 39.2 |  | 7 | 5.2
9.6 SWC5LD ESPA2MAX | 0 | 28k | 15 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 68 |  | 38.3 | 49.79 | 0.18576 | 0.24149 | 0.38 | 0.494 | 25.6 | 33.28 |  | 45 | 90 | 7 + 2 | 15000 | 15153 | 6839 |  | 8314 |  |  |  |  | 6666.7 |  |  | 1528 | [6 empty] | 1375 |  | 602.8 | 594.9 |  |  | 70.8 |  | 50.5 |  | 7.1 | 8.2
9.6 SWC5LD ESPA2MAX | 0 | 28k | 15 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 102.4 |  | 38.5 | 50.05 | 0.18673 | 0.24275 | 0.53 | 0.689 | 38.5 | 50.05 |  | 45 | 90 | 7 + 2 | 14881 | 14937 | 6741.6 |  | 8195.9 |  |  |  |  | 6666.7 |  |  | 555.6 | [6 empty] | 500 |  | 603.6 | 598.6 |  |  | 36.4 |  | 30.5 |  | 7 | 3
9.6 SWC5LD ESPA2MAX | 0 | 28k | 13 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 106.1 |  | 59.9 | 77.87 | 0.29053 | 0.37769 | 0.52 | 0.676 | 39.9 | 51.87 |  | 45 | 90 | 7 + 2 | 14848 | 14875 | 6713.3 |  | 8162 |  |  |  |  | 6666.7 |  |  | 277.8 | [6 empty] | 250 |  | 613.3 | 605.5 |  |  | 25.6 |  | 21.7 |  | 6.9 | 1.5
9.6 SWC5LD ESPA2MAX | 0 | 28k | 12 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 71 |  | 40.2 | 52.26 | 0.19498 | 0.25347 | 0.38 | 0.494 | 26.8 | 34.84 |  | 45 | 90 | 7 + 2 | 14949 | 15060 | 6797 |  | 8264 |  |  |  |  | 6666.7 |  |  | 1111 | [6 empty] | 1000 |  | 618.7 | 610.8 |  |  | 56.3 |  | 42.3 |  | 7
9.6 SWC5LD ESPA2MAX | 0 | 28k | 10 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 72 |  | 40.3 | 52.39 | 0.19546 | 0.2541 | 0.36 | 0.468 | 26.9 | 34.97 |  | 45 | 90 | 7 + 2 | 14924 | 15014 | 6776 |  | 8238 |  |  |  |  | 6666.7 |  |  | 903 | [6 empty] | 813 |  | 632.7 | 624.7 |  |  | 48.6 |  | 37.3 |  | 7 | 4.9
9.6 SWC5LD ESPA2MAX | 0 | 28k | 8 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 73 |  | 41 | 53.3 | 0.19886 | 0.25852 | 0.36 | 0.468 | 27.4 | 35.62 |  | 45 | 90 | 7 + 2 | 14980 | 14952 | 6749 |  | 8204 |  |  |  |  | 6666.7 |  |  | 625 | [6 empty] | 563 |  | 650.3 | 642.3 |  |  | 36.9 |  | 29.1 |  | 7 | 3.4
9.6 SWC5LD ESPA2MAX | 0 | 24k | 18 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 59.6 |  | 33.5 | 43.55 | 0.16248 | 0.21123 | 0.38 | 0.494 | 22.4 | 29.12 |  | 45 | 90 | 7 + 2 | 15043 | 15230 | 6873.9 |  | 8356.8 |  |  |  |  | 6666.7 |  |  | 1875 | [6 empty] | 1687.5 |  | 525.6 | 517.6 |  |  | 79.2 |  | 53.1 |  | 7.1 | 10.1
9.6 SWC5LD ESPA2MAX | 0 | 24k | 18 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 87.4 |  | 49.2 | 63.96 | 0.23863 | 0.31022 | 0.53 | 0.689 | 32.8 | 42.64 |  | 45 | 90 | 7 + 2 | 14920 | 15006 | 6772.9 |  | 8234 |  |  |  |  | 6666.7 |  |  | 868.1 | [6 empty] | 781.3 |  | 526.3 | 518.5 |  |  | 43.5 |  | 34 |  | 7 | 4.7
9.6 SWC5LD ESPA2MAX | 0 | 24k | 15 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 64 |  | 36.1 | 46.93 | 0.17509 | 0.22762 | 0.38 | 0.494 | 24.1 | 31.33 |  | 45 | 90 | 7 + 2 | 14983 | 15122 | 6825.2 |  | 8298 |  |  |  |  | 6666.7 |  |  | 1389 | [6 empty] | 1250 |  | 537 | 529.3 |  |  | 63.6 |  | 45.3 |  | 7 | 7.5
9.6 SWC5LD ESPA2MAX | 0 | 24k | 15 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 94.5 |  | 53.2 | 69.16 | 0.25803 | 0.33544 | 0.53 | 0.689 | 35.45 | 46.085 |  | 46 | 90 | 7 + 2 | 14865 | 14906 | 6727.7 |  | 8179 |  |  |  |  | 6666.7 |  |  | 416.7 | [6 empty] | 375 |  | 537.6 | 529.8 |  |  | 29.4 |  | 24.6 |  | 6.9 | 2.2
9.6 SWC5LD ESPA2MAX | 0 | 24k | 15 | 7 | 1 | 497 | 27 | 12 | 8 | 10.5 | 98.3 |  | 55.3 | 71.89 | 0.26822 | 0.34868 | 0.52 | 0.676 | 35.6 | 46.28 |  | 45 | 90 | 7 + 2 | 14856 | 14891 | 6720.7 |  | 8170.5 |  |  |  |  | 6666.7 |  |  | 347.2 | [6 empty] | 312.5 |  | 537.6 | 529.8 |  |  | 38.7 |  | 31 |  | 6.9 | 3.7
9.6 SWC5LD ESPA2MAX | 0 | 24k | 13 | 7 | "2/1" | wont converge
9.6 SWC5LD ESPA2MAX | 0 | 24k | 12 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 68 |  | 38.4 | 49.92 | 0.18625 | 0.24212 | 0.38 | 0.494 | 25.6 | 33.28 |  | 45 | 90 | 7 + 2 | 14924 | 15014 | 6776 |  | 8238 |  |  |  |  | 6666.7 |  |  | 903 | [6 empty] | 813 |  | 553.5 | 545.5 |  |  | 45.9 |  | 34.7 |  | 7 | 4.9
9.6 SWC5LD ESPA2MAX | 0 | 24k | 10 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 70 |  | 39.1 | 50.83 | 0.18964 | 0.24654 | 0.38 | 0.494 | 26.1 | 33.93 |  | 45 | 90 | 7 + 2 | 14890 | 14952 | 6749 |  | 8204 |  |  |  |  | 6666.7 |  |  | 625 | [6 empty] | 562 |  | 567.4 | 559.4 |  |  | 34.8 |  | 27.1 |  | 7 | 3.4
9.6 SWC5LD ESPA2MAX | 0 | 24k | 8 | 7 | 2 | 497 | 54 | 24 | 8 | 10.5 | 71 |  | 40 | 52 | 0.19401 | 0.25221 | 0.37 | 0.481 | 26.6 | 34.58 |  | 45 | 90 | 7 + 2 | 14856 | 14891 | 6721 |  | 8171 |  |  |  |  | 6666.7 |  |  | 347 | [6 empty] | 313 |  | 584.6 | 576.5 |  |  | 22.8 |  | 18 |  | 6.9 | 1.9
9.6 SWC5LD ESPA2MAX | 0 | 24k | 8 | 7 | 1 | 497 | 27 | 12 | 8 | 10.5 | 72 |  | 40.4 | 52.52 | 0.19595 | 0.25473 | 0.37 | 0.481 | 27 | 35.1 |  | 45 | 90 | 7 + 1 | 14848 | 14875 | 6713.7 |  | 8162 |  |  |  |  | 6666.7 |  |  | 277.8 | [6 empty] | 250 |  | 584.5 | 576.5 |  |  | 32.5 |  | 25.4 |  | 6.9 | 3
[15 empty] | Br to Cl psg | 1.3
Note on AV46: Steven Alt: Feed Pressure higher in Not to exceed case as 2nd pass ROC higher TDS and thus 1st pass ROF higher TDS
Note on Q57: Steven Alt: For TDS less than average, both bromide and chloride drop in the same proportion, so ok to keep /21000*71

## Equipment & Load List
9.6 MGD
[32 empty] | Load Type |  | Max KW | kW
[32 empty] | 1=continuous | Op time | over plant | during
P&ID tag | Title | Facility Name | General Description | Duty | Standby | Future | Unit Capacity | Motor Rated Horsepower | Voltage | Speed Control | Brake Horsepower | Unit Size | Total Duty Capacity | Equipment Type | Packaged Equipment | Total Connected Load (kW) | Total Expected Load (kW) | Standby Power Required | Control System | Additional FutureBuildout QTY | Materials of Construction | Other Features | A - Manufacturer | B - Manufacturers | Equipment Package Number | Contact Person | Modified | ID | EventAccessLevel | Item Type | Path | 2=Intermittent | hrs/day | life | Acc test
| Dilution Water Pump 1(for chem feed) |  |  | TRUE | FALSE |  |  | 20 | 480 | Constant | 0 |  |  | Process - Mechanical | FALSE | 14.914 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-10 10:47 | 28 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 14.914 | 14.914
| Dilution Water Pump 2 (for chem feed) |  |  | FALSE | TRUE |  |  | 20 | 480 | Constant | 0 |  |  | Process - Mechanical | FALSE | 14.914 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-10 10:48 | 29 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0 | standby
| VRF Cooling/Heating, 5.92 kW (8.2 A @ 480/3) | 10-Administration Building |  | TRUE | FALSE |  | 5.92 kW | 0 | 480 | Constant | 0 |  |  | HVAC | TRUE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 273 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List | 1 |  | 5.9 | 5.9
| DOAS Air Handler 18.5 FLA @480/3, 22.5 MCA | 10-Administration Building |  | TRUE | FALSE |  | 22.5 MCA | 0 | 480 | Constant | 0 |  |  | HVAC | TRUE | 18.7 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 275 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List | 1 |  | 18.7 | 18.7
| 10-EF-01, Lab Exhaust Fan | 10-Administration Building |  | TRUE | FALSE |  |  | 0.17 | 120 | Constant | 0.1 |  |  | HVAC | FALSE | 0.12677 | 0.07457 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 277 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List | 1 |  | 0.07457 | 0.07457
| VRF Indoor Fan Coil Units | 10-Administration Building |  | TRUE | FALSE |  | (12) units, 100 W each | 0 | 208 | Constant | 0 |  |  | Process - Mechanical | TRUE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 278 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List | 1 |  | 0 | 0
| VRF Branch Selector Unit | 10-Administration Building |  | TRUE | FALSE | FALSE | 178 W | 0 | 208 | Constant | 0 |  |  | Process - Mechanical | TRUE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:46 | 279 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List | 1 |  | 0 | 0
| 10-GUH-01, Unit Heater | 10-Administration Building |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 280 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List | 1 |  | 0.07457 | 0.07457
| 10-EF-02, Exhaust Fan | 10-Administration Building |  | TRUE | FALSE |  |  | 0.17 | 120 | Constant | 0.1 |  |  | Process - Mechanical | FALSE | 0.12677 | 0.07457 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 281 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List | 1 |  | 0.12677 | 0.12677
| Wafer Style Static Mixer | 24-Pretreatment Facility | Raw Water Metering Station | TRUE | FALSE |  |  | 0 |  | Constant | 0 | 30" flange |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 73 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
| Filter Controller | 24-Pretreatment Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 75 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
| Future Blowers + MCC Room 1 | 24-Pretreatment Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 129 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
| Future Blowers + MCC Room 2 | 24-Pretreatment Facility |  | FALSE | TRUE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 130 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
| Media Filter 1 | 24-Pretreatment Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 133 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
| Media Filter 2 | 24-Pretreatment Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 134 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
| Media Filter 3 | 24-Pretreatment Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 135 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
| Media Filter 4 | 24-Pretreatment Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 136 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
| Media Filter 5 | 24-Pretreatment Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 137 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
| Media Filter 6 | 24-Pretreatment Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 138 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
| Media Filter 7 | 24-Pretreatment Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 139 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
| Media Filter 8 | 24-Pretreatment Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 140 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
| Media Filter 9 | 24-Pretreatment Facility |  | FALSE | TRUE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 141 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
| Media Filter 10 | 24-Pretreatment Facility |  | FALSE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 142 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
| 24-SF-01/Supply Fan | 24-Pretreatment Facility |  | TRUE | FALSE |  |  | 2 | 208 | Variable | 1.1 |  |  | HVAC | FALSE | 1.4914 | 0.82027 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 184 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List | 1 |  | 1.4914 | 1.4914
| 24-SF-02/Supply Fan | 24-Pretreatment Facility |  | TRUE | FALSE |  |  | 3 | 208 | Variable | 1.8 |  |  | HVAC | FALSE | 2.2371 | 1.3423 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 185 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List | 1 |  | 2.2371 | 2.2371
| 24-EF-01/Exhaust Fan | 24-Pretreatment Facility |  | TRUE | FALSE |  |  | 1 | 208 | Variable | 0.6 |  |  | HVAC | FALSE | 0.7457 | 0.44742 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 213 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List | 1 |  | 0.7457 | 0.7457
| 24-EF-02/Exhaust Fan | 24-Pretreatment Facility |  | TRUE | FALSE |  |  | 2 | 208 | Variable | 1.1 |  |  | HVAC | FALSE | 1.4914 | 0.82027 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 214 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List | 1 |  | 1.4914 | 1.4914
| 24-GUH-01/Unit Heater | 24-Pretreatment Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 241 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List | 1 |  | 0.07457 | 0.07457
| 24-GUH-02/Unit Heater | 24-Pretreatment Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 242 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List | 1 |  | 0.07457 | 0.07457
| 24-ACU-01 Wall Mount AC Unit | 24-Pretreatment Facility | 18 MCA | TRUE | FALSE |  |  | 0 | 480 | Constant | 0 |  |  | HVAC | FALSE | 15 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-29 10:16 | 286 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List | 1 |  | 15 | 0 | Wont be running during acc test. Fans will be acceptable
24TNK751 | Polymer Feed Tank | 24-Pretreatment Facility |  | TRUE | FALSE | FALSE |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:19 | 321 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
24PMP761 | Non-Ionic Polymer Feed Pump 1 | 24-Pretreatment Facility |  | TRUE | FALSE | FALSE |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:19 | 322 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.2 | 0.2
24PMP762 | Non-Ionic Polymer Feed Pump 2 | 24-Pretreatment Facility |  | TRUE | FALSE | FALSE |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:19 | 323 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
28PMP201 | Backwash Supply Pump 1 | 28-Filtered Water & Backwash PS |  | TRUE | FALSE |  | 7540gpm @ 52' | 150 | 480 | Variable | 0 |  |  | Process - Mechanical | FALSE | 113 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:46 | 1 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 103.8369 | 103.8369
28PMP202 | Backwash Supply Pump 2 | 28-Filtered Water & Backwash PS |  | FALSE | TRUE |  | 7540gpm @ 52' | 150 | 480 | Variable | 0 |  |  | Process - Mechanical | FALSE | 113 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:47 | 2 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0 | standby
28PMP104 | Cartridge Filter Feed Pump 4 | 28-Filtered Water & Backwash PS |  | TRUE | FALSE |  | 7,673 gpm @ 80' | 200 | 480 | Constant | 0 |  |  | Process - Mechanical | FALSE | 298.2796 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 3 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
28PMP103 | Cartridge Filter Feed Pump 3 | 28-Filtered Water & Backwash PS |  | FALSE | TRUE |  | 7,673 gpm @ 80' | 200 | 480 | Constant | 0 |  |  | Process - Mechanical | FALSE | 298.2796 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 4 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
28PMP101 | Cartridge Filter Feed Pump 1 | 28-Filtered Water & Backwash PS |  | TRUE | FALSE |  | 3,837 gpm @ 80' | 125 | 480 | Variable | 0 |  |  | Process - Mechanical | FALSE | 186.4247 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 5 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
| Backwash Lagoons/ Sludge Drying Bed 1 | 28-Filtered Water & Backwash PS |  | TRUE | FALSE |  | 3,837 gpm @ 80' | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 102 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
| Backwash Lagoons/ Sludge Drying Bed 2 | 28-Filtered Water & Backwash PS |  | FALSE | TRUE |  | 3,837 gpm @ 80' | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 122 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
28PMP102 | Cartridge Filter Feed Pump 2 | 28-Filtered Water & Backwash PS |  | TRUE | FALSE |  | 3,837 gpm @ 80' | 125 | 480 | Variable | 0 |  |  | Process - Mechanical | FALSE | 186.4247 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-06 16:34 | 171 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
28PMP105 | Cartridge Filter Feed Pump 5 | 28-Filtered Water & Backwash PS |  | TRUE | FALSE | TRUE |  | 400 | 480 | Constant | 0 |  |  | Process - Mechanical | FALSE | 298.2796 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-06 16:58 | 304 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
37PMP101 | Recycle Pump 1 | 38-Recycle PS | Raw Water Recycle (RWR) at Backwash Waste Basins | TRUE | FALSE |  | 800 gpm @ 87 ft TDH | 35 | 480 | Variable | 0 | 800 gpm @ 87 ft TDH | 1600 gpm @ 87 ft TDH | Process - Mechanical | FALSE | 26.0995 | 0 | FALSE |  | 0 | FRP vinyl-ester resin | 1800 rpm | FYbroc 1500 size 4x6x13 | Vanton |  |  | 2013-08-07 15:47 | 34 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 18.4326 | 18.4326
37PMP102 | Recycle Pump 2 | 38-Recycle PS | Raw Water Recycle (RWR) at Backwash Waste Basins | TRUE | FALSE |  | 800 gpm @ 87 ft TDH | 35 | 480 | Variable | 0 | 800 gpm @ 87 ft TDH | 1600 gpm @ 87 ft TDH | Process - Mechanical | FALSE | 26.0995 | 0 | FALSE |  | 0 | FRP vinyl-ester resin | 1800 rpm | FYbroc 1500 size 4x6x13 | Vanton |  |  | 2013-08-07 15:53 | 35 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 18.4326 | 18.4326
37PMP103 | Recycle Pump 3 | 38-Recycle PS | Raw Water Recycle (RWR) at Backwash Waste Basins | FALSE | TRUE |  | 800 gpm @ 87 ft TDH | 35 | 480 | Variable | 0 | 800 gpm @ 87 ft TDH | 1600 gpm @ 87 ft TDH | Process - Mechanical | FALSE | 26.0995 | 0 | FALSE |  | 0 | FRP vinyl-ester resin | 1800 rpm | FYbroc 1500 size 4x6x13 | Vanton |  |  | 2013-08-07 16:42 | 284 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0 | standby
42PMP201 | 1st Pass RO Feed Pump 1 | 42-RO Facility |  | TRUE | FALSE |  |  | 1000 | 4160 | Variable | 0 |  |  | Process - Mechanical | FALSE | 932.1237 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:29 | 7 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
42PMP202 | 1st Pass RO Feed Pump 2 | 42-RO Facility |  | TRUE | FALSE |  |  | 1000 | 4160 | Variable | 0 |  |  | Process - Mechanical | FALSE | 932.1237 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:29 | 8 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
42PMP203 | 1st Pass RO Feed Pump 3 | 42-RO Facility |  | TRUE | FALSE |  |  | 1000 | 4160 | Variable | 0 |  |  | Process - Mechanical | FALSE | 932.1237 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:30 | 9 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
42PMP204 | 1st Pass RO Feed Pump 4 | 42-RO Facility |  | TRUE | FALSE |  |  | 1000 | 4160 | Variable | 0 |  |  | Process - Mechanical | FALSE | 932.1237 | 0 | FALSE | [8 empty] | 2013-08-07 16:30 | 10 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
42PMP205 | 1st Pass RO Feed Pump 5 | 42-RO Facility |  | TRUE | FALSE |  |  | 1000 | 4160 | Variable | 0 |  |  | Process - Mechanical | FALSE | 932.1237 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:30 | 11 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
42PMP206 | 1st Pass RO Feed Pump 6 | 42-RO Facility |  | TRUE | FALSE |  |  | 1000 | 4160 | Variable | 0 |  |  | Process - Mechanical | FALSE | 932.1237 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:30 | 12 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
42PMP207 | 1st Pass RO Feed Pump 7 | 42-RO Facility |  | FALSE | TRUE |  |  | 1000 | 4160 | Variable | 0 |  |  | Process - Mechanical | FALSE | 932.1237 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:29 | 13 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
42PMP401 | 1st Pass RO ERD Booster Feed Pump 1 | 42-RO Facility |  | TRUE | FALSE |  |  | 75 | 480 | Variable | 0 |  |  | Process - Mechanical | FALSE | 56.25 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:32 | 14 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
42PMP402 | 1st Pass RO ERD Booster Feed Pump 2 | 42-RO Facility |  | TRUE | FALSE |  |  | 75 | 480 | Variable | 0 |  |  | Process - Mechanical | FALSE | 56.25 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:32 | 15 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
42PMP403 | 1st Pass RO ERD Booster Feed Pump 3 | 42-RO Facility |  | TRUE | FALSE |  |  | 75 | 480 | Variable | 0 |  |  | Process - Mechanical | FALSE | 56.25 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:32 | 16 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
42PMP404 | 1st Pass RO ERD Booster Feed Pump 4 | 42-RO Facility |  | TRUE | FALSE |  |  | 75 | 480 | Variable | 0 |  |  | Process - Mechanical | FALSE | 56.25 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:32 | 17 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
42PMP405 | 1st Pass RO ERD Booster Feed Pump 5 | 42-RO Facility |  | TRUE | FALSE |  |  | 75 | 480 | Variable | 0 |  |  | Process - Mechanical | FALSE | 56.25 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:32 | 18 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
42PMP406 | 1st Pass RO ERD Booster Feed Pump 6 | 42-RO Facility |  | TRUE | FALSE |  |  | 75 | 480 | Variable | 0 |  |  | Process - Mechanical | FALSE | 56.25 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:32 | 19 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
42PMP407 | 1st Pass RO ERD Booster Feed Pump 7 | 42-RO Facility |  | FALSE | TRUE |  |  | 75 | 480 | Variable | 0 |  |  | Process - Mechanical | FALSE | 56.25 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:33 | 20 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
42PMP801 | RO Cleaning Pump | 42-RO Facility |  | TRUE | FALSE |  |  | 150 | 480 | Constant | 0 |  |  | Process - Mechanical | FALSE | 112.5 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:36 | 21 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List | 2 | 0.95342 | 106.7507 | 0 | No cleaning during acceptance test
42PMP901 | Neutralization Transfer Pump | 42-RO Facility |  | TRUE | FALSE |  |  | 75 | 480 | Constant | 0 |  |  | Process - Mechanical | FALSE | 55.9274 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:39 | 22 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List | 2 | 0.11918 | 45.4005 | 0 | No cleaning during acceptance test
42PMP511 | RO Flush Pump 1 | 42-RO Facility |  | FALSE | FALSE |  |  | 40 | 480 | Constant | 0 |  |  | Process - Mechanical | FALSE | 29.828 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:37 | 23 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List | 1 |  | 0 | 0 | These do not run when the RO is running
42PMP512 | RO Flush Pump 2 | 42-RO Facility |  | FALSE | TRUE |  |  | 40 | 480 | Constant | 0 |  |  | Process - Mechanical | FALSE | 29.828 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 12:07 | 24 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List | 1 |  | 0 | 0
42PMP701 | 2nd Pass HP Feed Pump 1 | 42-RO Facility |  | TRUE | FALSE |  |  | 200 | 480 | Variable | 0 |  |  | Process - Mechanical | FALSE | 149.1398 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 25 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
42PMP702 | 2nd Pass HP Feed Pump 2 | 42-RO Facility |  | TRUE | FALSE |  |  | 200 | 480 | Variable | 0 |  |  | Process - Mechanical | FALSE | 149.1398 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 26 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
42PMP951 | 1st pass trench submersible sump pump 1 | 42-RO Facility |  | TRUE | FALSE |  |  | 20 | 480 | Constant | 0 |  |  | Process - Mechanical | FALSE | 14.914 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:22 | 64 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List | 2 |  | 14.914 | 14.914
42PMP952 | 1st pass trench submersible sump pump 2 | 42-RO Facility |  | FALSE | TRUE |  |  | 20 | 480 | Constant | 0 |  |  | Process - Mechanical | FALSE | 14.914 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:22 | 65 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List | 2 |  | 14.914 | 0
42PMP961 | 2nd pass trench submersible sump pump 1 | 42-RO Facility |  | TRUE | FALSE |  |  | 20 | 480 | Constant | 0 |  |  | Process - Mechanical | FALSE | 14.914 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:22 | 66 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 14.914 | 14.914
42PMP962 | 2nd pass trench submersible sump pump 1 |  |  | FALSE | TRUE |  |  | 20 | 480 | Constant | 0 |  |  | Process - Mechanical | FALSE | 14.914 | 0 | [16 empty] | 14.914
| 1st pass RO train 71 x 7M Vessel 1 | 42-RO Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:22 | 78 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| 1st pass RO train 71 x 7M Vessel 2 | 42-RO Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:22 | 79 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| 1st pass RO train 71 x 7M Vessel 3 | 42-RO Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:22 | 80 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| 1st pass RO train 71 x 7M Vessel 4 | 42-RO Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 81 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| 1st pass RO train 71 x 7M Vessel 5 | 42-RO Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 82 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| 1st pass RO train 71 x 7M Vessel 6 | 42-RO Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:20 | 83 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| 1st pass RO train 71 x 7M Vessel 7 | 42-RO Facility |  | FALSE | TRUE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 84 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
42FLT111 | Cartridge Filter 1 | 42-RO Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 11:08 | 85 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
42FLT112 | Cartridge Filter 2 | 42-RO Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 11:08 | 86 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
42FLT113 | Cartridge Filter 3 | 42-RO Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 11:08 | 87 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
42FLT114 | Cartridge Filter 4 | 42-RO Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 11:08 | 88 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
42FLT115 | Cartridge Filter 5 | 42-RO Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 11:08 | 89 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
42FLT116 | Cartridge Filter 6 | 42-RO Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 11:08 | 90 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
42FLT117 | Cartridge Filter 7 | 42-RO Facility |  | FALSE | TRUE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 11:08 | 91 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| CIP Tank | 42-RO Facility |  | TRUE | FALSE |  | 10000 gal | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 92 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| CIP Tank Heater | 42-RO Facility |  | TRUE | FALSE |  | 200 kW | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 200 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 93 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List | 2 |  | 200 | 0 | No cleaning during acceptance test
42TNK911 | Discharge Neutralization Tank | 42-RO Facility |  | TRUE | FALSE |  | 32000 gal | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 12:22 | 94 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| Flush Tank | 42-RO Facility |  | TRUE | FALSE |  | 68000 gal | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 95 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| 2nd pass RO train 26 x 13 7M Vessel 1 | 42-RO Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 96 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| 2nd pass RO train 26 x 13 7M Vessel 2 | 42-RO Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 97 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| 2nd pass RO train 26 x 13 7M Vessel 3 | 42-RO Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 98 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| 42-SF-01/Supply Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 5 | 480 | Variable | 3.8 |  |  | HVAC | FALSE | 3.7285 | 2.8337 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 186 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 2.8337 | 2.8337
| 42-SF-02/Supply Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 5 | 480 | Variable | 3.8 |  |  | Process - Mechanical | FALSE | 3.7285 | 2.8337 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 189 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 2.8337 | 2.8337
| 42-SF-03/Supply Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 5 | 480 | Variable | 3.8 |  |  | HVAC | FALSE | 3.7285 | 2.8337 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 190 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 2.8337 | 2.8337
| 42-SF-02/Supply Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 5 | 480 | Variable | 3.8 |  |  | HVAC | FALSE | 3.7285 | 2.8337 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 191 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 2.8337 | 2.8337
| 42-SF-04/Supply Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 5 | 480 | Variable | 3.8 |  |  | HVAC | FALSE | 3.7285 | 2.8337 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 192 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 2.8337 | 2.8337
| 42-SF-05/Supply Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 5 | 480 | Variable | 3.8 |  |  | HVAC | FALSE | 3.7285 | 2.8337 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 193 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 2.8337 | 2.8337
| 42-SF-06/Supply Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 5 | 480 | Variable | 3.8 |  |  | HVAC | FALSE | 3.7285 | 2.8337 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 194 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 2.8337 | 2.8337
| 42-SF-07/Supply Fan | 42-RO Facility |  | FALSE | TRUE |  |  | 5 | 480 | Variable | 3.8 |  |  | HVAC | FALSE | 3.7285 | 2.8337 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 195 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 2.8337 | 2.8337
| 42-SF-08/Supply Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 2 | 480 | Variable | 1.7 |  |  | HVAC | FALSE | 1.4914 | 1.2677 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 196 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 1.2677 | 1.2677
| 42-SF-09/Supply Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 2 | 480 | Variable | 1.7 |  |  | HVAC | FALSE | 1.4914 | 1.2677 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 197 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 1.2677 | 1.2677
| 42-SF-10/Supply Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 2 | 480 | Variable | 1.7 |  |  | HVAC | FALSE | 1.4914 | 1.2677 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 198 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 1.2677 | 1.2677
| 42-SF-11/Supply Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 7.5 | 480 | Variable | 5.9 |  |  | HVAC | FALSE | 5.5927 | 4.3996 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 199 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 4.3996 | 4.3996
| 42-SF-12/Supply Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 7.5 | 480 | Variable | 5.9 |  |  | HVAC | FALSE | 5.5927 | 4.3996 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 200 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 4.3996 | 4.3996
| 42-SF-13/Supply Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 7.5 | 480 | Variable | 5.9 |  |  | HVAC | FALSE | 5.5927 | 4.3996 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 200 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 4.3996 | 4.3996
| 42-SF-13/Supply Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 7.5 | 480 | Variable | 5.9 |  |  | HVAC | FALSE | 5.5927 | 4.3996 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 200 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 4.3996 | 4.3996
| 42-EF-01/Exhaust Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 3 | 480 | Variable | 2.4 |  |  | HVAC | FALSE | 2.2371 | 1.7897 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 215 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 1.7897 | 1.7897
| 42-EF-02/Exhaust Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 3 | 480 | Variable | 2.4 |  |  | HVAC | FALSE | 2.2371 | 1.7897 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 216 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 1.7897 | 1.7897
| 42-EF-03/Exhaust Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 3 | 480 | Variable | 2.4 |  |  | HVAC | FALSE | 2.2371 | 1.7897 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 217 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 1.7897 | 1.7897
| 42-EF-04/Exhaust Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 3 | 480 | Variable | 2.4 |  |  | HVAC | FALSE | 2.2371 | 1.7897 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 218 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 1.7897 | 1.7897
| 42-EF-05/Exhaust Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 3 | 480 | Variable | 2.4 |  |  | HVAC | FALSE | 2.2371 | 1.7897 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 219 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 1.7897 | 1.7897
| 42-EF/06/Exhaust Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 3 | 480 | Variable | 2.4 |  |  | HVAC | FALSE | 2.2371 | 1.7897 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 220 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 1.7897 | 1.7897
| 42-EF-07/Exhaust Fan | 42-RO Facility |  | FALSE | TRUE |  |  | 3 | 480 | Variable | 2.4 |  |  | HVAC | FALSE | 2.2371 | 1.7897 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 221 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 1.7897 | 1.7897
| 42-EF-08/Exhaust Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 2 | 480 | Variable | 1.1 |  |  | HVAC | FALSE | 1.4914 | 0.82027 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 222 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.82027 | 0.82027
| 42-EF-09/Exhaust Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 2 | 480 | Variable | 1.1 |  |  | HVAC | FALSE | 1.4914 | 0.82027 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 223 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.82027 | 0.82027
| 42-EF-10/Exhaust Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 2 | 480 | Variable | 1.1 |  |  | HVAC | FALSE | 1.4914 | 0.82027 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 224 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.82027 | 0.82027
| 42-EF-11/Exhaust Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 5 | 480 | Variable | 3.7 |  |  | HVAC | FALSE | 3.7285 | 2.7591 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 225 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 2.7591 | 2.7591
| 42-EF-12/Exhaust Fan | 42-RO Facility |  | FALSE | TRUE |  |  | 5 | 480 | Variable | 3.7 |  |  | HVAC | FALSE | 3.7285 | 2.7591 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 226 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 2.7591 | 2.7591
| 42-EF-13/Exhaust Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 5 | 480 | Variable | 3.7 |  |  | HVAC | FALSE | 3.7285 | 2.7591 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 227 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 2.7591 | 2.7591
| 42-EF-14/Exhaust Fan | 42-RO Facility |  | FALSE | TRUE |  |  | 5 | 480 | Variable | 3.7 |  |  | HVAC | FALSE | 3.7285 | 2.7591 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 228 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 2.7591 | 2.7591
| 42-GUH-01/Unit Heater | 42-RO Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 243 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0.07457
| 42-GUH-02/Unit Heater | 42-RO Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 244 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0.07457
| 42-GUH-03/Unit Heater | 42-RO Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 245 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0.07457
| 42-GUH-04/Unit Heater | 42-RO Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 246 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0.07457
| 42-GUH-05/Unit Heater | 42-RO Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 247 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0.07457
| 42-GUH-06/Unit Heater | 42-RO Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 248 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0.07457
| 42-GUH-07/Unit Heater | 42-RO Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 249 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0.07457
| 42-GUH-08/Unit Heater | 42-RO Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 250 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0.07457
| 42-GUH-09/Unit Heater | 42-RO Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 251 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0.07457
| 42-GUH-10/Unit Heater | 42-RO Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 252 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0.07457
| 42-GUH-11/Unit Heater | 42-RO Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 253 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0.07457
| 42-GUH-12/Unit Heater | 42-RO Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 254 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0.07457
| 42-GUH-13/Unit Heater | 42-RO Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 255 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0.07457
| 42-GUH-14/Unit Heater | 42-RO Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 256 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0.07457
| 42-GUH-15/Unit Heater | 42-RO Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 257 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0.07457
| 42-GUH-16/Unit Heater | 42-RO Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 258 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0.07457
| 42-GUH-17/Unit Heater | 42-RO Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 259 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0.07457
| 42-GUH-18/Unit Heater | 42-RO Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 260 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0.07457
| 42-GUH-19/Unit Heater | 42-RO Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 261 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0.07457
| 42-GUH-20/Unit Heater | 42-RO Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 262 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0.07457
| 2nd pass trench submersible sump pump 2 | 42-RO Facility |  | FALSE | TRUE |  |  | 20 | 480 | Constant | 0 |  |  | Process - Mechanical | FALSE | 14.914 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 274 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 14.914 | 0
| Single element RO test stand | 42-RO Facility |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 276 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| 42-SF-13, Supply Fan | 42-RO Facility |  | TRUE | FALSE |  |  | 0.17 |  | Constant | 0.1 |  |  | HVAC | FALSE | 0.12677 | 0.07457 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 282 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0.07457
| 42-ACU-01 Wall Mount AC Unit | 42-RO Facility | 23 MCA | TRUE | FALSE |  |  | 0 | 480 | Constant | 0 |  |  | HVAC | FALSE | 19 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-29 10:16 | 287 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 19 | 0 | Wont be running during acc test. Fans will be acceptable
| 42-ACU-02 Wall Mount AC Unit | 42-RO Facility | 23 MCA | TRUE | FALSE |  |  | 0 | 480 | Constant | 0 |  |  | HVAC | FALSE | 19 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-29 10:17 | 288 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 19 | 0 | Wont be running during acc test. Fans will be acceptable
| 42-ACU-03 Wall Mount AC Unit | 42-RO Facility | 23 MCA | TRUE | FALSE |  |  | 0 | 480 | Constant | 0 |  |  | HVAC | FALSE | 19 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-29 10:18 | 289 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 19 | 0 | Wont be running during acc test. Fans will be acceptable
| 42-ACU-04 Wall Mount AC Unit | 42-RO Facility | 23 MCA | TRUE | FALSE |  |  | 0 | 480 | Constant | 0 |  |  | HVAC | FALSE | 19 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-29 10:18 | 290 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 19 | 0 | Wont be running during acc test. Fans will be acceptable
| 42-ACU-05 Wall Mount AC Unit | 42-RO Facility | 23 MCA | TRUE | FALSE |  |  | 0 | 480 | Constant | 0 |  |  | HVAC | FALSE | 19 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-29 10:18 | 291 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0 | Wont be running during acc test. Fans will be acceptable
| 42-ACU-06 Wall Mount AC Unit | 42-RO Facility | 23 MCA | TRUE | FALSE |  |  | 0 | 480 | Constant | 0 |  |  | HVAC | FALSE | 19 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-29 10:18 | 292 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0 | Wont be running during acc test. Fans will be acceptable
| 42-ACU-07 Wall Mount AC Unit | 42-RO Facility | 23 MCA | TRUE | FALSE |  |  | 0 | 480 | Constant | 0 |  |  | HVAC | FALSE | 19 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-29 10:18 | 293 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0 | Wont be running during acc test. Fans will be acceptable
| 42-ACU-08 Wall Mount AC Unit | 42-RO Facility | 23 MCA | TRUE | FALSE |  |  | 0 | 480 | Constant | 0 |  |  | HVAC | FALSE | 19 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-29 10:18 | 294 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0 | Wont be running during acc test. Fans will be acceptable
| 42-ACU-09 Wall Mount AC Unit | 42-RO Facility | 23 MCA | TRUE | FALSE |  |  | 0 | 480 | Constant | 0 |  |  | HVAC | FALSE | 19 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-29 10:18 | 295 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0 | Wont be running during acc test. Fans will be acceptable
42PMP208 | 1st Pass HP Feed Pump 8 | 42-RO Facility |  | TRUE | FALSE | TRUE |  | 1250 | 4160 | Variable | 0 |  |  | Process - Mechanical | FALSE | 932.1237 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-06 16:32 | 299 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
42PMP209 | 1st Pass HP Feed Pump 9 | 42-RO Facility |  | TRUE | FALSE | TRUE |  | 1250 | 4160 | Variable | 0 |  |  | Process - Mechanical | FALSE | 932.1237 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-06 16:32 | 300 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| 1st Pass ERD Recir Pump 8 | 42-RO Facility |  | TRUE | FALSE | TRUE |  | 125 | 480 | Variable | 0 |  |  | Process - Mechanical | FALSE | 93.2124 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-06 16:32 | 301 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| 1st Pass ERD Recir Pump 9 | 42-RO Facility |  | TRUE | FALSE | TRUE |  | 125 | 480 | Variable | 0 |  |  | Process - Mechanical | FALSE | 93.2124 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-06 16:32 | 302 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| 2nd Pass HP Feed Pump 4 | 42-RO Facility |  | TRUE | FALSE | TRUE |  | 200 | 480 | Variable | 0 |  |  | Process - Mechanical | FALSE | 149.1398 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-06 16:33 | 303 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
42TNK501 | RO FLUSH INTERMEDIATE PERMEATE TANK | 42-RO Facility |  | TRUE | FALSE | FALSE |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 12:07 | 309 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
42PMP701 | RO Membrane Feed Pump | 42-RO Facility |  | TRUE | FALSE | FALSE |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 12:13 | 311 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
42TNK811 | RO Membrane Cleaning Tank | 42-RO Facility |  | TRUE | FALSE | FALSE |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 12:15 | 312 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
44PMP761 | Polymer Feed Pump 1 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.25 | 120 | Variable |  |  |  | Process - Mechanical | FALSE | 0.18642 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:25 | 38 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.18642 | 0.18642
44PMP762 | Polymer Feed Pump 2 | 44-Chemical Facility |  | FALSE | TRUE |  |  | 0.25 | 120 | Variable |  |  |  | Process - Mechanical | FALSE | 0.18642 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:26 | 39 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0 | standby
44PMP401 | Sodium Hypochlorite Addition Pump 1 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.75 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.55927 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-08 09:42 | 40 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.55927 | 0.55927
44PMP402 | Sodium Hypochlorite Addition Pump 2 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.75 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.55927 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-08 09:43 | 41 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.55927 | 0.55927
44PMP403 | Sodium Hypochlorite Addition Pump 3 | 44-Chemical Facility |  | TRUE | FALSE | FALSE |  | 0.75 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.55927 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-08 09:43 | 42 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
44PMP404 | Sodium Hypochlorite Addition Pump 4 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.5 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-08 09:43 | 43 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.37285 | 0 | filter BW
44PMP601 | Sodium Bisulfite Addition Pump 1 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.5 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:14 | 44 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.37285 | 0.37285
44PMP602 | Sodium Bisulfite Addition Pump 2 | 44-Chemical Facility |  | FALSE | TRUE |  |  | 0.5 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:14 | 45 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
44PMP101 | Sulfuric Acid Feed Pump 1 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.5 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 46 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.37285 | 0 | We will not use this
44PMP102 | Sulfuric Acid Feed Pump 2 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.5 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 47 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0 | We will not use this
44PMP201 | Threshold Inhibitor Addition Pump 1 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.5 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:50 | 48 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.37285 | 0.37285
44PMP202 | Threshold Inhibitor Addition Pump 2 | 44-Chemical Facility |  | FALSE | TRUE |  |  | 0.5 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:51 | 49 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.37285 | 0.37285
44PMP203 | Threshold Inhibitor Addition Pump 3 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.5 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:51 | 50 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0 | standby
44PSH204 | Threshold Inhibitor Addition Pump 4 | 44-Chemical Facility |  | FALSE | TRUE |  |  | 0.25 | 120 | Variable |  |  |  | Process - Mechanical | FALSE | 0.18642 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:51 | 51 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.18642 | 0 | 4,5 second pass
44PMP301 | Sodium Hydroxide Addition Pump 1 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.5 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:52 | 52 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.37285 | 0.37285
44PMP302 | Sodium Hydroxide Addition Pump 2 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.5 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:52 | 53 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.37285 | 0.37285
44PMP303 | Sodium Hydroxide Addition Pump 3 | 44-Chemical Facility |  | FALSE | TRUE |  |  | 0.5 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:53 | 54 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
44PMP304 | Sodium Hydroxide Transfer Pump 1 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.5 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:54 | 55 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
44PMP701 | Zink Orthophosphate Addition Pump 1 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.25 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.18642 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:15 | 56 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.18642 | 0.18642
44PMP702 | Zink Orthophosphate Addition Pump 2 | 44-Chemical Facility |  | FALSE | TRUE |  |  | 0.25 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.18642 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:15 | 57 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
44PMP501 | Lime Slurry Pump 1 | 44-Chemical Facility |  | TRUE | FALSE |  |  |  | 480 | Variable |  |  |  | Process - Mechanical | TRUE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:22 | 58 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.37285 | 0.37285
44PMP502 | Lime Slurry Pump 2 | 44-Chemical Facility |  | FALSE | TRUE |  |  |  | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:23 | 59 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0 | standby
| Polymer Drum | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0 |  | Constant |  |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 105 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| Hypochlorite Brine Tank 1 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0 |  | Constant |  |  |  | Process - Mechanical | TRUE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 107 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| Hypochlorite Generator 1 | 44-Chemical Facility |  | TRUE | FALSE |  | 90 A |  | 480 | Constant |  |  |  | Process - Mechanical | TRUE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 108 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 90 | 90 | per A Chang, all 3 for 8 hrs/day
| Hypochlorite Solution Tank 1 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0 |  | Constant |  |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 109 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
44TNK611 | Bisulfite Tank | 44-Chemical Facility |  | TRUE | FALSE | FALSE |  | 0 |  | Constant |  |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 08:59 | 110 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
44TNK111 | Sulfuric Acid Tank | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0 |  | Constant |  |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 11:31 | 111 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
44TNK211 | Threshold Inhibitor Tank | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0 |  | Constant |  |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:50 | 112 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
44TNK311 | Sodium Hydroxide Tank | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0 |  | Constant |  |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:53 | 113 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
44TNK711 | Zink Orthophosphate Tank | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0 |  | Constant |  |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 114 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| Hydrated Lime Silo & Slaking System | 44-Chemical Facility |  | TRUE | FALSE |  | 60 A |  | 480 | Constant |  |  |  | Process - Mechanical | TRUE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 115 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 60 | 60 | per A Chang
44TNK801 | Carbon Dioxide Storage Tank 1 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 6 | 480 | Constant |  |  |  | Process - Mechanical | TRUE | 4.4742 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:21 | 116 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| Hypochlorite Solution Tank 2 | 44-Chemical Facility |  | FALSE | TRUE |  |  | 0 |  | Constant |  |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 118 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| Hypochlorite Generator 2 | 44-Chemical Facility |  | TRUE | FALSE |  | 90 A |  | 480 | Constant |  |  |  | Process - Mechanical | TRUE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 119 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 90 | 90 | per A Chang, all 3 for 8 hrs/day
| Hypochlorite Generator 3 | 44-Chemical Facility |  | TRUE | FALSE |  | 90 A |  | 480 | Constant |  |  |  | Process - Mechanical | TRUE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 120 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 90 | 90 | per A Chang, all 3 for 8 hrs/day
| Hypochlorite Brine Tank 2 | 44-Chemical Facility |  | FALSE | TRUE |  |  | 0 |  | Constant |  |  |  | Process - Mechanical | TRUE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 121 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| Polymer Blend System | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.33 | 120 | Constant |  |  |  | Process - Mechanical | TRUE | 0.24608 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 148 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
44PMP405 | Sodium Hypochlorite Addition Pump 5 | 44-Chemical Facility |  | FALSE | TRUE |  |  | 0.5 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-08 09:44 | 149 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0 | standby for filter BW
44PMP406 | Sodium Hypochlorite Addtion Pump 6 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.5 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-08 09:44 | 150 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.37285 | 0.37285 | post treat
44PMP407 | Sodium Hypochlorite Addition Pump 7 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.5 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-08 09:44 | 151 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | standby post treat
44PMP603 | Sodium Bisulfite Addition Pump 3 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.5 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:15 | 152 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
44PMP103 | Sulfuric Acid Feed Pump 3 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.5 |  | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:42 | 153 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.37285 | 0
44PMP104 | Sulfuric Acid Feed Pump 4 | 44-Chemical Facility |  | FALSE | TRUE |  |  | 0.5 |  | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:43 | 154 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.37285 | 0
44PMP105 | Sulfuric Acid Transfer Pump 1 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.5 |  | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:49 | 155 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0 | transfer pump
| Sulfuric Acid Feed Pump 6 | 44-Chemical Facility |  | FALSE | TRUE |  |  | 0.5 |  | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 156 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | negligible
44PSH205 | Threshold Inhibitor Addition Pump 5 | 44-Chemical Facility |  | FALSE | TRUE |  |  | 0.25 | 120 | Variable |  |  |  | Process - Mechanical | FALSE | 0.18642 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:52 | 157 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0 | standby
| Hydrated Lime Silo Heater 1 | 44-Chemical Facility |  | TRUE | FALSE |  | 10 kW |  | 480 | Constant |  |  |  | Process - Mechanical | TRUE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 158 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 10 | 10
| Hydrated Lime Silo Heater 2 | 44-Chemical Facility |  | TRUE | FALSE |  | 10 kW |  | 480 | Constant |  |  |  | Process - Mechanical | TRUE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 159 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 10 | 0
| Hydrated Lime Silo Exhaust Fan | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.3 | 120 | Constant |  |  |  | Process - Mechanical | TRUE | 0.22371 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 160 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.22371 | 0.22371
| Hydrated Lime Silo Unloading LCP | 44-Chemical Facility |  | TRUE | FALSE |  | 30 A |  |  | Constant |  |  |  | Process - Mechanical | TRUE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 161 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
| Hydrated Lime Silo Damper | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.3 | 120 | Constant |  |  |  | Process - Mechanical | TRUE | 0.22371 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 162 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.22371 | 0.22371
| Zink Orthophosphate Feed Pump 3 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.25 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.18642 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 163 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| Zink Orthophosphate Feed Pump 4 | 44-Chemical Facility |  | FALSE | TRUE |  |  | 0.25 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.18642 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 164 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
44PMP305 | Sodium Hydroxide Addition Pump 4 | 44-Chemical Facility |  | FALSE | TRUE |  |  | 0.5 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:56 | 165 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.37285 | 0.37285
44PMP306 | Sodium Hydroxide Addition Pump 5 | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.5 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:57 | 166 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| Sodium Hydroxide Feed Pump 7 | 44-Chemical Facility |  | FALSE | TRUE |  |  | 0.5 | 480 | Variable |  |  |  | Process - Mechanical | FALSE | 0.37285 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 167 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| Carbon Dioxide Vaporizer 1 | 44-Chemical Facility |  | TRUE | FALSE |  | 12 kW |  | 480 | Constant |  |  |  | Process - Mechanical | TRUE | 12 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 174 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 12 | 12 | Runs continuously per A change
| Carbon Dioxide Vaporizer 2 | 44-Chemical Facility |  | FALSE | TRUE |  | 12 kW |  | 480 | Constant |  |  |  | Process - Mechanical | TRUE | 12 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 175 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0 | Standby
| Carbon Dioxide Vapor Heater 1 | 44-Chemical Facility |  | TRUE | FALSE |  | 4 kW |  | 480 | Constant |  | 1 ph (not 3 ph) |  | Process - Mechanical | TRUE | 4 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 176 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 4 | 4 | Runs continuously per A change
| Carbon Dioxide Vapor Heater 2 | 44-Chemical Facility |  | FALSE | TRUE |  | 4 kW |  | 480 | Constant |  | 1 ph (not 3 ph) |  | Process - Mechanical | TRUE | 4 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 177 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0 | Standby
| Hypochlorite Water Heater 1 | 44-Chemical Facility |  | TRUE | FALSE |  | 27 kW |  |  | Constant |  |  |  | Process - Mechanical | TRUE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 178 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 27 | 27 | 2 x 12 hrs each per A chang
| Hypochlorite Water Heater 2 | 44-Chemical Facility |  | TRUE | FALSE |  | 27 kW |  |  | Constant |  |  |  | Process - Mechanical | TRUE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 179 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 27 | 27 | 2 x 12 hrs each per A chang
| Hypochlorite Water Heater 3 | 44-Chemical Facility |  | TRUE | FALSE |  | 27 kW |  |  | Constant |  |  |  | Process - Mechanical | TRUE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 180 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0 | Standby
| Hypochlorite Tank 1 Blower | 44-Chemical Facility |  | TRUE | FALSE |  |  | 1 | 480 | Constant |  |  |  | Process - Mechanical | TRUE | 0.7457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 181 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.7457 | 0.7457
44BLR402 | Hypochlorite Tank 2 Blower | 44-Chemical Facility |  | TRUE | FALSE |  |  | 1 | 480 | Constant |  |  |  | Process - Mechanical | TRUE | 0.7457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 182 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.7457 | 0.7457
44BLR401 | Hypochlorite Generation Blower | 44-Chemical Facility |  | TRUE | FALSE |  |  | 1 | 480 | Constant |  |  |  | Process - Mechanical | TRUE | 0.7457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 183 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.7457 | 0.7457
| 44-SF-01/Supply Fan | 44-Chemical Facility |  | TRUE | FALSE |  |  | 1 | 208 | Variable | 0.7 |  |  | HVAC | FALSE | 0.7457 | 0.52199 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 201 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.52199 | 0.52199
| 44-SF-02/Supply Fan | 44-Chemical Facility |  | TRUE | FALSE |  |  | 1 | 208 | Variable | 0.7 |  |  | HVAC | FALSE | 0.7457 | 0.52199 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 202 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.52199 | 0.52199
| 44-SF-03/Supply Fan | 44-Chemical Facility |  | TRUE | FALSE |  |  | 1 | 208 | Variable | 0.7 |  |  | HVAC | FALSE | 0.7457 | 0.52199 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 203 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.52199 | 0.52199
| 44-SF-04/Supply Fan | 44-Chemical Facility |  | TRUE | FALSE |  |  | 1 | 208 | Variable | 0.7 |  |  | HVAC | FALSE | 0.7457 | 0.52199 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 204 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.52199 | 0.52199
| 44-SF-05/Supply Fan | 44-Chemical Facility |  | TRUE | FALSE |  |  | 1 | 208 | Variable | 0.7 |  |  | HVAC | FALSE | 0.7457 | 0.52199 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 205 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.52199 | 0.52199
| 44-SF-06/Supply Fan | 44-Chemical Facility |  | TRUE | FALSE |  |  | 2 | 208 | Variable | 1.4 |  |  | HVAC | FALSE | 1.4914 | 1.044 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 206 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 1.044 | 1.044
| 44-SF-07/Supply Fan | 44-Chemical Facility |  | TRUE | FALSE |  |  | 7.5 | 480 | Variable | 4.7 |  |  | HVAC | FALSE | 5.5927 | 3.5048 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 207 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 3.5048 | 3.5048
| 44-SF-08/Supply Fan | 44-Chemical Facility |  | TRUE | FALSE |  |  | 2 | 208 | Variable | 1.8 |  |  | HVAC | FALSE | 1.4914 | 1.3423 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 209 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 1.3423 | 1.3423
| 44-EF-01/Exhaust Fan | 44-Chemical Facility |  | TRUE | FALSE |  |  | 1 | 480 | Variable | 0.5 |  |  | HVAC | FALSE | 0.7457 | 0.37285 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 229 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.37285 | 0.37285
| 44-EF-02/Exhaust Fan | 44-Chemical Facility |  | TRUE | FALSE |  |  | 1 | 480 | Variable | 0.5 |  |  | HVAC | FALSE | 0.7457 | 0.37285 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 230 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.37285 | 0.37285
| 44-EF-03/Exhaust Fan | 44-Chemical Facility |  | TRUE | FALSE |  |  | 1 | 480 | Variable | 0.5 |  |  | HVAC | FALSE | 0.7457 | 0.37285 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 231 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.37285 | 0.37285
| 44-EF-04/Exhaust Fan | 44-Chemical Facility |  | TRUE | FALSE |  |  | 1 | 480 | Variable | 0.5 |  |  | HVAC | FALSE | 0.7457 | 0.37285 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 232 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.37285 | 0.37285
| 44-EF-05/Exhaust Fan | 44-Chemical Facility |  | TRUE | FALSE |  |  | 1 | 480 | Variable | 0.5 |  |  | HVAC | FALSE | 0.7457 | 0.37285 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 233 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.37285 | 0.37285
| 44-EF-06/Exhaust Fan | 44-Chemical Facility |  | TRUE | FALSE |  |  | 2 | 480 | Variable | 0.9 |  |  | HVAC | FALSE | 1.4914 | 0.67113 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 234 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.67113 | 0.67113
| 44-EF-07/Exhaust Fan | 44-Chemical Facility |  | TRUE | FALSE |  |  | 5 | 480 | Variable | 2.9 |  |  | HVAC | FALSE | 3.7285 | 2.1625 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 235 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 2.1625 | 2.1625
| 44-GUH-01/Unit Heater | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 263 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0
| 44-GUH-02/Unit Heater | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 264 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0
| 44-GUH-03/Unit Heater | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 265 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0
| 44-GUH-04/Unit Heater | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 266 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0
| 44-GUH-05/Unit Heater | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 267 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0
| 44-GUH-06/Unit Heater | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 268 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0
| 44-GUH-07/Unit Heater | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 269 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0
| 44-GUH-08/Unit Heater | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 270 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0
| 44-GUH-09/Unit Heater | 44-Chemical Facility |  | TRUE | FALSE |  |  | 0.1 | 120 | Constant | 0 |  |  | HVAC | FALSE | 0.07457 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 271 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.07457 | 0
| Sodium Hydroxide Tank Heater | 44-Chemical Facility | Need to determine low density heat tracing req. | TRUE | FALSE |  | 45 kW |  | 480 | Constant |  |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 285 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 45 | 0 | Assume not running during acc test
| 44-ACU-01 Wall Mount AC Unit | 44-Chemical Facility | 18 MCA | TRUE | FALSE |  |  | 0 | 480 | Constant | 0 |  |  | HVAC | FALSE | 15 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-29 10:18 | 296 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 15 | 0 | Wont be running during acc test. Fans will be acceptable
44PMP105 | Sulfuric Acid Transfer Pump 1 | 44-Chemical Facility |  | TRUE | FALSE | FALSE |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 12:40 | 315 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
44TNK411 | Sodium Hypochlorite Tank | 44-Chemical Facility |  | TRUE | FALSE | FALSE |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 12:45 | 317 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
44TNK412 | Sodium Hypochlorite Tank | 44-Chemical Facility |  | TRUE | FALSE | FALSE |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 12:45 | 318 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
44PMP604 | Sodium Bisulfite Feed Pump 4 | 44-Chemical Facility |  | TRUE | FALSE | FALSE |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:11 | 319 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
44PMP605 | Sodium Bisulfite Feed Pump 5 | 44-Chemical Facility |  | TRUE | FALSE | FALSE |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:12 | 320 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0
52UVU101 | UV Disenfection Unit No. 1 | 52-UV Facility |  | TRUE | FALSE |  | 20kW |  | 480 | Constant | 0 |  |  | Process - Mechanical | TRUE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:40 | 62 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 12.6 | 12.6
52UVU102 | UV Disenfection Unit No. 2 | 52-UV Facility |  | FALSE | TRUE |  | 20kW | 0 | 480 | Constant | 0 |  |  | Process - Mechanical | TRUE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 16:40 | 63 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0 | standby
| 52-SF-01/Supply Fan | 52-UV Facility |  | TRUE | FALSE |  |  | 2 | 208 | Variable | 0.9 |  |  | HVAC | FALSE | 1.4914 | 0.67113 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 210 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.67113 | 0.67113
| 52-SF-02/Supply Fan | 52-UV Facility |  | TRUE | FALSE |  |  | 0.75 | 208 | Variable | 0.3 |  |  | HVAC | FALSE | 0.55927 | 0.22371 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 211 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0.22371 | 0.22371
58PMP101 | Finished Water Pump 1 | 58-Finished Water PS |  | TRUE | FALSE |  | 1,670 gpm @ 325' | 250 | 480 | Variable | 0 |  |  | Process - Mechanical | FALSE | 186.4247 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:38 | 30 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
58PMP102 | Finished Water Pump 2 | 58-Finished Water PS |  | TRUE | FALSE |  | 1,670 gpm @ 325' | 250 | 480 | Variable | 0 |  |  | Process - Mechanical | FALSE | 186.4247 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:38 | 31 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
58PMP103 | Finished Water Pump 3 | 58-Finished Water PS |  | TRUE | FALSE |  | 3,335 gpm @ 325' | 400 | 480 | Constant | 0 |  |  | Process - Mechanical | FALSE | 298.2796 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:38 | 32 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
58PMP104 | Finished Water Pump 4 | 58-Finished Water PS |  | FALSE | TRUE |  | 3,335 gpm @ 325' | 400 | 480 | Constant | 0 |  |  | Process - Mechanical | FALSE | 298.2796 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:38 | 33 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  |  |  | see pump calcs page
58TNK111 | Finished Water Receiving Tank 1 | 58-Finished Water PS |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 12:25 | 131 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
58TNK112 | Finished Water Receiving Tank 2 | 58-Finished Water PS |  | FALSE | TRUE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 12:25 | 132 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
58PMP201 | Salinas Valley Desal Transfer Pump 1 | 58-Finished Water PS | (hp not confirmed) | TRUE | FALSE |  | 835 gpm @ 30' | 25 | 480 | Variable | 0 |  |  | Process - Mechanical | FALSE | 18.75 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:38 | 172 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 14.8622 | 0 | We shall not run these pumps during the acceptance test
58PMP202 | Salinas Valley Desal Transfer Pump 2 | 58-Finished Water PS | (hp not confirmed) | TRUE | FALSE |  | 835 gpm @ 30' | 25 | 480 | Variable | 0 |  |  | Process - Mechanical | FALSE | 18.75 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:39 | 173 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 14.8622 | 0 | We shall not run these pumps during the acceptance test
58PMP105 | Finished Water Pump 4 | 58-Finished Water PS |  | TRUE | FALSE | TRUE |  | 400 | 480 | Constant | 0 |  |  | Process - Mechanical | FALSE | 298.2796 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-06 16:36 | 305 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| 60-SF-01/Supply Fan | 60-Finished Water EE Bldg |  | TRUE | FALSE |  |  | 2 | 208 | Variable | 1.7 |  |  | HVAC | FALSE | 1.4914 | 1.2677 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 212 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 1.2677 | 1.2677
| 60-ACU-01 Wall Mount AC Unit | 60-Finished Water EE Bldg | 18 | TRUE | FALSE |  |  | 0 | 480 | Constant | 0 |  |  | HVAC | FALSE | 15 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-29 10:19 | 298 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 15 | 0 | Wont be running during acc test. Fans will be acceptable
| Brine Storage Basin | 67-Brine Storage Pond |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 103 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
68PMP101 | Brine Pump 1 | 68-Brine PS |  | TRUE | FALSE |  |  | 60 | 480 | Constant | 0 | 4167 gpm @ 30 ft TDH | 4167 gpm @ 30 ft TDH | Process - Mechanical | FALSE | 44.7419 | 0 | FALSE |  |  | FRP vinyl-ester resin | 1200 rpm | FYbroc 1500 size 10x12x6 | Vanton |  |  | 2013-08-07 10:15 | 36 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 81.5855 | 0 | Wont be running these pumps during acceptance test
68PMP102 | Brine Pump 2 | 68-Brine PS |  | FALSE | TRUE |  |  | 60 | 480 | Constant | 0 | 4167 gpm @ 30 ft TDH | 4167 gpm @ 30 ft TDH | Process - Mechanical | FALSE | 44.7419 | 0 | FALSE |  | 0 | FRP vinyl-ester resin | 1200 rpm | FYbroc 1500 size 10x12x6 | Vanton |  |  | 2013-08-07 10:15 | 37 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List |  |  | 0 | 0 | standby
| Lime Feed System | Other |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 99 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| Wafter Style Static Mixer | Other | Mixing Injection Station on Treated Water line | TRUE | FALSE |  |  | 0 |  | Constant | 0 | 20" flange |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 100 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| ALT: Calcite Upflow Contactor 1 | Other |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 123 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| ALT: Calcite Upflow Contactor 2 | Other |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 124 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| ALT: Calcite Upflow Contactor 3 | Other |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 125 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| ALT: Calcite Upflow Contactor 4 | Other |  | TRUE | FALSE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 126 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| ALT: Calcite Upflow Contactor 5 | Other |  | TRUE | TRUE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-08-07 10:27 | 127 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
| ALT: Calcite Upflow Contactor 6 | Other |  | FALSE | TRUE |  |  | 0 |  | Constant | 0 |  |  | Process - Mechanical | FALSE | 0 | 0 | FALSE |  | 0 | [6 empty] | 2013-07-26 11:21 | 128 | 5 | Item | proposals/MontereyDesalinationWTP/Lists/Equipment List
[33 empty] | Total | 1419.9684 | 733.4164
[33 empty] | Total | 3.5503 | 1.8337 | kwh/1000 gal
| Transformer losses | [32 empty] | 90 | 90 |  | From Ryan
[33 empty] | Xfmr loss | 0.22502 |  | kwh/1000 gal
[32 empty] | Melbourne | Xfrmr loss | 0.7182 |  | kwh/1000 gal
Note on AI64: Steven Alt: 8 hours per CIP per train. 1st pass every 4 months. 2nd pass every 2 years.
Note on AI65: Steven Alt: 1 hour per CIP
Note on AJ262: Steven Alt: per Kim Ervin